## Slide 1: NPRR1128: Changes to Ensure Critical FFR Participation
Shams Siddiqi, Ph.D.
Representing Hunt Energy Network
(512) 619-3532
shams@crescentpower.net
WMS Meeting
June 1, 2022
Notes: <number>

## Slide 2: Ideal Responsive Resource Service
<number>
Ideal RRS provision:
  Resources timely responding to frequency drop (or increase) providing precisely the amount of response required based on 100% responsive capacity deployed with 1% change in frequency
  Resources timely un-deploying frequency response in an amount based precisely the current level of frequency deviation
  And this timely precise response should be the same regardless of system inertia
ESRs can provide this ideal response capability with fast response time and precise calculated MW response at any system inertia level
  GRs and ONSC Hydros have slower response times – a real concern during lower inertia
  Load Resource response is imprecise (bulky) and cannot be rearmed quickly for next event (freeing up non-PRC capacity does not adequately protect against next frequency event)
ESR response is ideal for any system inertia and critical for lower inertia
  GRs and Hydros too slow to timely arrest frequency – reflected in “Equivalence Factors”
  Lower inertia in 2021 compared to past years and significant IRRs being built in next few years
  450MW of FFR can lower Critical Inertia from 100 GW*s to 90 GW*s
What’s wrong with ESRs providing PFR-RRS?
  ONSC Hydro PFR-RRS has a frequency trigger of 59.8 Hz and 20 seconds to respond – likely too slow for when frequency is that low.
  Other PFR-RRS responds when frequency outside +/-17 mHz: ESRs’ fast response implies ESRs bear disproportionate PFR burden – better suited for GR PFR and not duration limited ESR
Notes: <number>

## Slide 3: Alternatives to get desired ESR RRS
<number>
Set wider frequency deadband for ESR to account for fast response:
  Since ESRs can provide PFR MWs based on 1% droop within a second, set PFR frequency deadband wider for Resources that can provide PFR MW with 0.5 sec response time.
  This will more equitably distribute PFR from fast responding ESRs and slower responding GRs
Allow ESRs to use ONSC status to provide RRS
  ESRs act like Synchronous Condensers and can deploy much faster than Hydros
  Make ONSC status technology neutral – even require 0.25 sec response for non-hydros (compared to 20 sec for hydros) to make the product much more useful in arresting frequency
NPRR1128: Create separate FFR category of RRS while maintaining max FFR limit (450MW):
  FFR is like ONSC except frequency trigger is 59.85Hz and response time is 15 cycles
  ONSC is not prorated with UFR-RRS and does not have a max limit
  FFR is far superior to ONSC-RRS as a service to timely arrest frequency
  Setting FFR offer floor at -$0.01/MWh is the least costly way to implement this change
Note: GR, LR, Hydro better suited for energy to restore load-gen balance:
  GRs and LRs (by the end of May 2022) can provide in 4,000+ MW Non-Spin market
  In 2023, GRs and LRs will be able to provide ECRS
LRs providing UFR-RRS currently have no incentive to qualify/provide FFR
In FAS (9/27/13), ERCOT wanted to require minimum amount of FFR when necessary to assure acceptable system response
Notes: <number>

## Slide 4: NPRR1128: Realize FFR Value
<number>
Even though FFR is a more valuable service designed for duration-limited ESRs and ESRs would rather provide FFR, the financial incentives are such that NO FFR has been provided to date (available since March 2020).
PUCT has discussed the importance of addressing inertia concerns and prioritized FFR advancement in their Phase I implementation.
NPRR1128 sets FFR offer floor at -$0.01/MWh – simple, minimal cost, quick
PFR-RRS, FFR and UFR-RRS would still receive the same MCPC; however, the incentive for ESRs and eligible LRs to provide FFR is no proration until 450MW limit is reached in awarded FFR quantity.
FFR Advancements, although helpful, still maintains current FFR proration
450MW of ESR providing FFR instead of PFR-RRS:
  Lowers critical inertia by 8-10 GW*s
  Likely increases system inertia due to additional commitment of GRs to provide PFR-RRS
  Increases reliability - FFR is reserved whereas PFR may be depleted if freq. drags for long time
With about 30GW of additional solar and 11GW of additional wind in CDR, inertia may be low any time of year/day – forecasting year-ahead difficult
Keeping NPRR1128 simple for low cost and quick implementation preferred
Notes: <number>