## 2026 Regulation Up
2026 Regulation-Up
HE | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
1 | 371 | 391 | 392 | 444 | 413 | 460 | 436 | 347 | 334 | 434 | 407 | 366
2 | 336 | 322 | 373 | 413 | 381 | 387 | 363 | 293 | 274 | 380 | 354 | 330
3 | 344 | 357 | 390 | 426 | 441 | 419 | 374 | 254 | 259 | 333 | 374 | 325
4 | 349 | 354 | 374 | 371 | 353 | 366 | 377 | 259 | 251 | 335 | 339 | 329
5 | 336 | 330 | 344 | 362 | 305 | 379 | 382 | 261 | 256 | 377 | 331 | 344
6 | 362 | 350 | 317 | 390 | 348 | 419 | 325 | 300 | 267 | 338 | 316 | 320
7 | 347 | 390 | 337 | 365 | 414 | 426 | 385 | 337 | 278 | 335 | 331 | 337
8 | 383 | 418 | 447 | 460 | 503 | 538 | 504 | 454 | 352 | 322 | 498 | 445
9 | 468 | 641 | 657 | 790 | 660 | 637 | 694 | 611 | 701 | 611 | 725 | 556
10 | 595 | 652 | 741 | 664 | 595 | 632 | 636 | 539 | 703 | 848 | 668 | 547
11 | 508 | 528 | 650 | 559 | 595 | 674 | 539 | 469 | 616 | 617 | 585 | 531
12 | 503 | 595 | 622 | 593 | 529 | 646 | 564 | 468 | 515 | 579 | 655 | 492
13 | 532 | 577 | 606 | 697 | 676 | 682 | 637 | 511 | 692 | 569 | 561 | 520
14 | 547 | 694 | 651 | 677 | 635 | 741 | 609 | 638 | 601 | 647 | 654 | 591
15 | 599 | 643 | 729 | 669 | 797 | 758 | 616 | 681 | 743 | 673 | 720 | 725
16 | 588 | 631 | 821 | 825 | 742 | 838 | 752 | 745 | 755 | 666 | 743 | 642
17 | 665 | 656 | 904 | 794 | 829 | 801 | 787 | 738 | 835 | 683 | 904 | 692
18 | 699 | 711 | 904 | 884 | 937 | 802 | 769 | 702 | 764 | 603 | 495 | 346
19 | 301 | 386 | 718 | 706 | 699 | 703 | 710 | 621 | 599 | 598 | 306 | 240
20 | 260 | 329 | 464 | 585 | 587 | 613 | 628 | 517 | 422 | 279 | 359 | 256
21 | 297 | 334 | 309 | 337 | 402 | 473 | 417 | 284 | 320 | 347 | 351 | 287
22 | 312 | 340 | 320 | 313 | 382 | 359 | 339 | 305 | 277 | 383 | 349 | 302
23 | 298 | 313 | 281 | 375 | 394 | 381 | 346 | 305 | 282 | 364 | 320 | 331
24 | 316 | 355 | 368 | 405 | 387 | 381 | 342 | 251 | 269 | 336 | 315 | 326
Total | 10316 | 11297 | 12719 | 13104 | 13004 | 13515 | 12531 | 10890 | 11365 | 11657 | 11660 | 10180

## 2026 Regulation Down
2026 Regulation-Down
HE | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
1 | 325 | 335 | 392 | 394 | 375 | 398 | 381 | 340 | 392 | 386 | 353 | 332
2 | 279 | 287 | 295 | 346 | 305 | 304 | 258 | 259 | 260 | 294 | 250 | 258
3 | 287 | 300 | 343 | 337 | 261 | 289 | 272 | 234 | 252 | 277 | 310 | 252
4 | 291 | 294 | 349 | 344 | 275 | 300 | 239 | 260 | 289 | 246 | 262 | 270
5 | 300 | 272 | 298 | 314 | 313 | 277 | 289 | 243 | 280 | 277 | 268 | 294
6 | 312 | 275 | 315 | 292 | 354 | 243 | 276 | 272 | 253 | 279 | 299 | 268
7 | 293 | 358 | 308 | 278 | 331 | 230 | 288 | 286 | 270 | 292 | 290 | 290
8 | 278 | 413 | 355 | 428 | 425 | 445 | 337 | 367 | 372 | 310 | 435 | 316
9 | 607 | 632 | 604 | 577 | 624 | 526 | 543 | 514 | 504 | 693 | 657 | 611
10 | 520 | 530 | 613 | 647 | 640 | 609 | 691 | 656 | 577 | 595 | 683 | 639
11 | 499 | 618 | 562 | 616 | 693 | 578 | 663 | 712 | 617 | 567 | 623 | 543
12 | 491 | 566 | 622 | 617 | 688 | 705 | 532 | 635 | 682 | 667 | 586 | 510
13 | 431 | 543 | 533 | 652 | 710 | 549 | 525 | 558 | 604 | 606 | 577 | 444
14 | 462 | 509 | 536 | 595 | 556 | 621 | 541 | 548 | 607 | 588 | 599 | 553
15 | 489 | 491 | 605 | 641 | 618 | 691 | 562 | 525 | 584 | 633 | 539 | 522
16 | 461 | 555 | 570 | 622 | 593 | 678 | 595 | 587 | 610 | 667 | 537 | 542
17 | 490 | 599 | 529 | 562 | 584 | 628 | 634 | 662 | 638 | 652 | 533 | 473
18 | 386 | 462 | 573 | 580 | 719 | 641 | 573 | 668 | 697 | 607 | 463 | 388
19 | 331 | 478 | 545 | 609 | 613 | 562 | 496 | 637 | 601 | 438 | 478 | 371
20 | 291 | 390 | 462 | 535 | 528 | 431 | 486 | 453 | 394 | 425 | 406 | 305
21 | 267 | 325 | 436 | 488 | 466 | 406 | 422 | 416 | 390 | 453 | 296 | 319
22 | 269 | 312 | 360 | 373 | 446 | 341 | 380 | 361 | 321 | 372 | 296 | 311
23 | 291 | 272 | 336 | 297 | 373 | 306 | 304 | 269 | 318 | 320 | 266 | 256
24 | 327 | 310 | 318 | 345 | 320 | 304 | 278 | 292 | 266 | 287 | 245 | 304
Total | 8977 | 10126 | 10859 | 11489 | 11810 | 11062 | 10565 | 10754 | 10778 | 10931 | 10251 | 9371

## 2026 RRS
2026 RRS
HE | Jan | Feb | Mar | Apr | May | Jun | July | Aug | Sep | Oct | Nov | Dec
1 | 2648 | 3036 | 3073 | 2986 | 2648 | 2516 | 2426 | 2300 | 2426 | 2702 | 2986 | 2945
2 | 2648 | 3036 | 3073 | 2986 | 2648 | 2516 | 2426 | 2300 | 2426 | 2702 | 2986 | 2945
3 | 2770 | 3073 | 3150 | 3073 | 2702 | 2597 | 2465 | 2344 | 2465 | 2770 | 3073 | 2945
4 | 2770 | 3073 | 3150 | 3073 | 2702 | 2597 | 2465 | 2344 | 2465 | 2770 | 3073 | 2945
5 | 2770 | 3073 | 3150 | 3073 | 2702 | 2597 | 2465 | 2344 | 2465 | 2770 | 3073 | 2945
6 | 2770 | 3073 | 3150 | 3073 | 2702 | 2597 | 2465 | 2344 | 2465 | 2770 | 3073 | 2945
7 | 2702 | 3036 | 3150 | 3073 | 2702 | 2597 | 2465 | 2344 | 2465 | 2770 | 3036 | 2867
8 | 2702 | 3036 | 3150 | 3073 | 2702 | 2597 | 2465 | 2344 | 2465 | 2770 | 3036 | 2867
9 | 2702 | 3036 | 3150 | 3073 | 2702 | 2597 | 2465 | 2344 | 2465 | 2770 | 3036 | 2867
10 | 2702 | 3036 | 3150 | 3073 | 2702 | 2597 | 2465 | 2344 | 2465 | 2770 | 3036 | 2867
11 | 2770 | 3073 | 3189 | 3150 | 2702 | 2516 | 2426 | 2344 | 2465 | 2867 | 3073 | 2986
12 | 2770 | 3073 | 3189 | 3150 | 2702 | 2516 | 2426 | 2344 | 2465 | 2867 | 3073 | 2986
13 | 2770 | 3073 | 3189 | 3150 | 2702 | 2516 | 2426 | 2344 | 2465 | 2867 | 3073 | 2986
14 | 2770 | 3073 | 3189 | 3150 | 2702 | 2516 | 2426 | 2344 | 2465 | 2867 | 3073 | 2986
15 | 2648 | 2986 | 3073 | 3036 | 2597 | 2465 | 2381 | 2300 | 2381 | 2702 | 2986 | 2867
16 | 2648 | 2986 | 3073 | 3036 | 2597 | 2465 | 2381 | 2300 | 2381 | 2702 | 2986 | 2867
17 | 2648 | 2986 | 3073 | 3036 | 2597 | 2465 | 2381 | 2300 | 2381 | 2702 | 2986 | 2867
18 | 2648 | 2986 | 3073 | 3036 | 2597 | 2465 | 2381 | 2300 | 2381 | 2702 | 2986 | 2867
19 | 2597 | 2945 | 2986 | 2867 | 2560 | 2426 | 2381 | 2300 | 2344 | 2597 | 2867 | 2702
20 | 2597 | 2945 | 2986 | 2867 | 2560 | 2426 | 2381 | 2300 | 2344 | 2597 | 2867 | 2702
21 | 2597 | 2945 | 2986 | 2867 | 2560 | 2426 | 2381 | 2300 | 2344 | 2597 | 2867 | 2702
22 | 2597 | 2945 | 2986 | 2867 | 2560 | 2426 | 2381 | 2300 | 2344 | 2597 | 2867 | 2702
23 | 2648 | 3036 | 3073 | 2986 | 2648 | 2516 | 2426 | 2300 | 2426 | 2702 | 2986 | 2945
24 | 2648 | 3036 | 3073 | 2986 | 2648 | 2516 | 2426 | 2300 | 2426 | 2702 | 2986 | 2945
Total | 64540 | 72596 | 74484 | 72740 | 63644 | 60468 | 58176 | 55728 | 58184 | 65632 | 72084 | 69248
These 2026 quantities above are based on the 2026 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW, the minimum RRS-PFR limit of 1377 MW and a floor of 2300 MW for all hours. Note that, NERC’s 2025 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows an increase in ERCOT’s IFRO. This is primarily because of an update in the IFRO methodology that was approved as a part of the Project 2017-01, Modifications to BAL-003. As a result of this ERCOT the minimum RRS-PFR limit for 2026 has been changed to align with ERCOT's new IFRO.

## 2026 RRS Table
These 2026 quantities above are based on the 2026 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW, the minimum RRS-PFR limit of 1377 MW and a floor of 2300 MW for all hours. Note that, NERC’s 2025 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows an increase in ERCOT’s IFRO. This is primarily because of an update in the IFRO methodology that was approved as a part of the Project 2017-01, Modifications to BAL-003. As a result of this ERCOT the minimum RRS-PFR limit for 2026 has been changed to align with ERCOT's new IFRO.
2026-01-01 | [5 empty] | 2026-02-01 | [5 empty] | 2026-03-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2648 | 1377 | 1271 | 1.28 | 48% | 1 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 1 | 3073 | 1377 | 1696 | 1.74 | 55.19%
2 | 2648 | 1377 | 1271 | 1.28 | 48% | 2 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 2 | 3073 | 1377 | 1696 | 1.74 | 55.19%
3 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 3 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 3 | 3150 | 1377 | 1773 | 1.83 | 56.29%
4 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 4 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 4 | 3150 | 1377 | 1773 | 1.83 | 56.29%
5 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 5 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 5 | 3150 | 1377 | 1773 | 1.83 | 56.29%
6 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 6 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 6 | 3150 | 1377 | 1773 | 1.83 | 56.29%
7 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 7 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 7 | 3150 | 1377 | 1773 | 1.83 | 56.29%
8 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 8 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 8 | 3150 | 1377 | 1773 | 1.83 | 56.29%
9 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 9 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 9 | 3150 | 1377 | 1773 | 1.83 | 56.29%
10 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 10 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 10 | 3150 | 1377 | 1773 | 1.83 | 56.29%
11 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 11 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 11 | 3189 | 1377 | 1812 | 1.94 | 56.82%
12 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 12 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 12 | 3189 | 1377 | 1812 | 1.94 | 56.82%
13 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 13 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 13 | 3189 | 1377 | 1812 | 1.94 | 56.82%
14 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 14 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 14 | 3189 | 1377 | 1812 | 1.94 | 56.82%
15 | 2648 | 1377 | 1271 | 1.28 | 48% | 15 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 15 | 3073 | 1377 | 1696 | 1.74 | 55.19%
16 | 2648 | 1377 | 1271 | 1.28 | 48% | 16 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 16 | 3073 | 1377 | 1696 | 1.74 | 55.19%
17 | 2648 | 1377 | 1271 | 1.28 | 48% | 17 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 17 | 3073 | 1377 | 1696 | 1.74 | 55.19%
18 | 2648 | 1377 | 1271 | 1.28 | 48% | 18 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 18 | 3073 | 1377 | 1696 | 1.74 | 55.19%
19 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 19 | 2945 | 1377 | 1568 | 1.51 | 53.24% | 19 | 2986 | 1377 | 1609 | 1.58 | 53.88%
20 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 20 | 2945 | 1377 | 1568 | 1.51 | 53.24% | 20 | 2986 | 1377 | 1609 | 1.58 | 53.88%
21 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 21 | 2945 | 1377 | 1568 | 1.51 | 53.24% | 21 | 2986 | 1377 | 1609 | 1.58 | 53.88%
22 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 22 | 2945 | 1377 | 1568 | 1.51 | 53.24% | 22 | 2986 | 1377 | 1609 | 1.58 | 53.88%
23 | 2648 | 1377 | 1271 | 1.28 | 48% | 23 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 23 | 3073 | 1377 | 1696 | 1.74 | 55.19%
24 | 2648 | 1377 | 1271 | 1.28 | 48% | 24 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 24 | 3073 | 1377 | 1696 | 1.74 | 55.19%
2026-04-01 | [5 empty] | 2026-05-01 | [5 empty] | 2026-06-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 1 | 2648 | 1377 | 1271 | 1.28 | 48% | 1 | 2516 | 1377 | 1139 | 1.15 | 45.27%
2 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 2 | 2648 | 1377 | 1271 | 1.28 | 48% | 2 | 2516 | 1377 | 1139 | 1.15 | 45.27%
3 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 3 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 3 | 2597 | 1377 | 1220 | 1.24 | 46.98%
4 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 4 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 4 | 2597 | 1377 | 1220 | 1.24 | 46.98%
5 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 5 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 5 | 2597 | 1377 | 1220 | 1.24 | 46.98%
6 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 6 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 6 | 2597 | 1377 | 1220 | 1.24 | 46.98%
7 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 7 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 7 | 2597 | 1377 | 1220 | 1.24 | 46.98%
8 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 8 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 8 | 2597 | 1377 | 1220 | 1.24 | 46.98%
9 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 9 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 9 | 2597 | 1377 | 1220 | 1.24 | 46.98%
10 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 10 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 10 | 2597 | 1377 | 1220 | 1.24 | 46.98%
11 | 3150 | 1377 | 1773 | 1.83 | 56.29% | 11 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 11 | 2516 | 1377 | 1139 | 1.15 | 45.27%
12 | 3150 | 1377 | 1773 | 1.83 | 56.29% | 12 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 12 | 2516 | 1377 | 1139 | 1.15 | 45.27%
13 | 3150 | 1377 | 1773 | 1.83 | 56.29% | 13 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 13 | 2516 | 1377 | 1139 | 1.15 | 45.27%
14 | 3150 | 1377 | 1773 | 1.83 | 56.29% | 14 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 14 | 2516 | 1377 | 1139 | 1.15 | 45.27%
15 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 15 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 15 | 2465 | 1377 | 1088 | 1.12 | 44.14%
16 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 16 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 16 | 2465 | 1377 | 1088 | 1.12 | 44.14%
17 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 17 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 17 | 2465 | 1377 | 1088 | 1.12 | 44.14%
18 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 18 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 18 | 2465 | 1377 | 1088 | 1.12 | 44.14%
19 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 19 | 2560 | 1377 | 1183 | 1.19 | 46.21% | 19 | 2426 | 1377 | 1049 | 1.08 | 43.24%
20 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 20 | 2560 | 1377 | 1183 | 1.19 | 46.21% | 20 | 2426 | 1377 | 1049 | 1.08 | 43.24%
21 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 21 | 2560 | 1377 | 1183 | 1.19 | 46.21% | 21 | 2426 | 1377 | 1049 | 1.08 | 43.24%
22 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 22 | 2560 | 1377 | 1183 | 1.19 | 46.21% | 22 | 2426 | 1377 | 1049 | 1.08 | 43.24%
23 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 23 | 2648 | 1377 | 1271 | 1.28 | 48% | 23 | 2516 | 1377 | 1139 | 1.15 | 45.27%
24 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 24 | 2648 | 1377 | 1271 | 1.28 | 48% | 24 | 2516 | 1377 | 1139 | 1.15 | 45.27%
2026-07-01 | [5 empty] | 2026-08-01 | [5 empty] | 2026-09-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2426 | 1377 | 1049 | 1.08 | 43.24% | 1 | 2300 | 1377 | 923 | 1 | 40.13% | 1 | 2426 | 1377 | 1049 | 1.08 | 43.24%
2 | 2426 | 1377 | 1049 | 1.08 | 43.24% | 2 | 2300 | 1377 | 923 | 1 | 40.13% | 2 | 2426 | 1377 | 1049 | 1.08 | 43.24%
3 | 2465 | 1377 | 1088 | 1.12 | 44.14% | 3 | 2344 | 1377 | 967 | 1.01 | 41.25% | 3 | 2465 | 1377 | 1088 | 1.12 | 44.14%
4 | 2465 | 1377 | 1088 | 1.12 | 44.14% | 4 | 2344 | 1377 | 967 | 1.01 | 41.25% | 4 | 2465 | 1377 | 1088 | 1.12 | 44.14%
5 | 2465 | 1377 | 1088 | 1.12 | 44.14% | 5 | 2344 | 1377 | 967 | 1.01 | 41.25% | 5 | 2465 | 1377 | 1088 | 1.12 | 44.14%
6 | 2465 | 1377 | 1088 | 1.12 | 44.14% | 6 | 2344 | 1377 | 967 | 1.01 | 41.25% | 6 | 2465 | 1377 | 1088 | 1.12 | 44.14%
7 | 2465 | 1377 | 1088 | 1.12 | 44.14% | 7 | 2344 | 1377 | 967 | 1.01 | 41.25% | 7 | 2465 | 1377 | 1088 | 1.12 | 44.14%
8 | 2465 | 1377 | 1088 | 1.12 | 44.14% | 8 | 2344 | 1377 | 967 | 1.01 | 41.25% | 8 | 2465 | 1377 | 1088 | 1.12 | 44.14%
9 | 2465 | 1377 | 1088 | 1.12 | 44.14% | 9 | 2344 | 1377 | 967 | 1.01 | 41.25% | 9 | 2465 | 1377 | 1088 | 1.12 | 44.14%
10 | 2465 | 1377 | 1088 | 1.12 | 44.14% | 10 | 2344 | 1377 | 967 | 1.01 | 41.25% | 10 | 2465 | 1377 | 1088 | 1.12 | 44.14%
11 | 2426 | 1377 | 1049 | 1.08 | 43.24% | 11 | 2344 | 1377 | 967 | 1.01 | 41.25% | 11 | 2465 | 1377 | 1088 | 1.12 | 44.14%
12 | 2426 | 1377 | 1049 | 1.08 | 43.24% | 12 | 2344 | 1377 | 967 | 1.01 | 41.25% | 12 | 2465 | 1377 | 1088 | 1.12 | 44.14%
13 | 2426 | 1377 | 1049 | 1.08 | 43.24% | 13 | 2344 | 1377 | 967 | 1.01 | 41.25% | 13 | 2465 | 1377 | 1088 | 1.12 | 44.14%
14 | 2426 | 1377 | 1049 | 1.08 | 43.24% | 14 | 2344 | 1377 | 967 | 1.01 | 41.25% | 14 | 2465 | 1377 | 1088 | 1.12 | 44.14%
15 | 2381 | 1377 | 1004 | 1.04 | 42.17% | 15 | 2300 | 1377 | 923 | 1 | 40.13% | 15 | 2381 | 1377 | 1004 | 1.04 | 42.17%
16 | 2381 | 1377 | 1004 | 1.04 | 42.17% | 16 | 2300 | 1377 | 923 | 1 | 40.13% | 16 | 2381 | 1377 | 1004 | 1.04 | 42.17%
17 | 2381 | 1377 | 1004 | 1.04 | 42.17% | 17 | 2300 | 1377 | 923 | 1 | 40.13% | 17 | 2381 | 1377 | 1004 | 1.04 | 42.17%
18 | 2381 | 1377 | 1004 | 1.04 | 42.17% | 18 | 2300 | 1377 | 923 | 1 | 40.13% | 18 | 2381 | 1377 | 1004 | 1.04 | 42.17%
19 | 2381 | 1377 | 1004 | 1.04 | 42.17% | 19 | 2300 | 1377 | 923 | 1 | 40.13% | 19 | 2344 | 1377 | 967 | 1.01 | 41.25%
20 | 2381 | 1377 | 1004 | 1.04 | 42.17% | 20 | 2300 | 1377 | 923 | 1 | 40.13% | 20 | 2344 | 1377 | 967 | 1.01 | 41.25%
21 | 2381 | 1377 | 1004 | 1.04 | 42.17% | 21 | 2300 | 1377 | 923 | 1 | 40.13% | 21 | 2344 | 1377 | 967 | 1.01 | 41.25%
22 | 2381 | 1377 | 1004 | 1.04 | 42.17% | 22 | 2300 | 1377 | 923 | 1 | 40.13% | 22 | 2344 | 1377 | 967 | 1.01 | 41.25%
23 | 2426 | 1377 | 1049 | 1.08 | 43.24% | 23 | 2300 | 1377 | 923 | 1 | 40.13% | 23 | 2426 | 1377 | 1049 | 1.08 | 43.24%
24 | 2426 | 1377 | 1049 | 1.08 | 43.24% | 24 | 2300 | 1377 | 923 | 1 | 40.13% | 24 | 2426 | 1377 | 1049 | 1.08 | 43.24%
2026-10-01 | [5 empty] | 2026-11-01 | [5 empty] | 2026-12-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 1 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 1 | 2945 | 1377 | 1568 | 1.51 | 53.24%
2 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 2 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 2 | 2945 | 1377 | 1568 | 1.51 | 53.24%
3 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 3 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 3 | 2945 | 1377 | 1568 | 1.51 | 53.24%
4 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 4 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 4 | 2945 | 1377 | 1568 | 1.51 | 53.24%
5 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 5 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 5 | 2945 | 1377 | 1568 | 1.51 | 53.24%
6 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 6 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 6 | 2945 | 1377 | 1568 | 1.51 | 53.24%
7 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 7 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 7 | 2867 | 1377 | 1490 | 1.44 | 51.97%
8 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 8 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 8 | 2867 | 1377 | 1490 | 1.44 | 51.97%
9 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 9 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 9 | 2867 | 1377 | 1490 | 1.44 | 51.97%
10 | 2770 | 1377 | 1393 | 1.39 | 50.29% | 10 | 3036 | 1377 | 1659 | 1.65 | 54.64% | 10 | 2867 | 1377 | 1490 | 1.44 | 51.97%
11 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 11 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 11 | 2986 | 1377 | 1609 | 1.58 | 53.88%
12 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 12 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 12 | 2986 | 1377 | 1609 | 1.58 | 53.88%
13 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 13 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 13 | 2986 | 1377 | 1609 | 1.58 | 53.88%
14 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 14 | 3073 | 1377 | 1696 | 1.74 | 55.19% | 14 | 2986 | 1377 | 1609 | 1.58 | 53.88%
15 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 15 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 15 | 2867 | 1377 | 1490 | 1.44 | 51.97%
16 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 16 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 16 | 2867 | 1377 | 1490 | 1.44 | 51.97%
17 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 17 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 17 | 2867 | 1377 | 1490 | 1.44 | 51.97%
18 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 18 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 18 | 2867 | 1377 | 1490 | 1.44 | 51.97%
19 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 19 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 19 | 2702 | 1377 | 1325 | 1.33 | 49.04%
20 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 20 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 20 | 2702 | 1377 | 1325 | 1.33 | 49.04%
21 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 21 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 21 | 2702 | 1377 | 1325 | 1.33 | 49.04%
22 | 2597 | 1377 | 1220 | 1.24 | 46.98% | 22 | 2867 | 1377 | 1490 | 1.44 | 51.97% | 22 | 2702 | 1377 | 1325 | 1.33 | 49.04%
23 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 23 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 23 | 2945 | 1377 | 1568 | 1.51 | 53.24%
24 | 2702 | 1377 | 1325 | 1.33 | 49.04% | 24 | 2986 | 1377 | 1609 | 1.58 | 53.88% | 24 | 2945 | 1377 | 1568 | 1.51 | 53.24%

## 2026 NSRS
2026 NSRS
HE | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
1 | 2281 | 2045 | 1455 | 1850 | 3188 | 2564 | 2009 | 1817 | 1878 | 2805 | 2371 | 3709
2 | 3112 | 2205 | 2849 | 2583 | 3229 | 2374 | 1433 | 1564 | 1795 | 2535 | 2371 | 2342
3 | 3147 | 2597 | 2955 | 2580 | 3410 | 2520 | 1611 | 2877 | 1673 | 2276 | 2451 | 2330
4 | 3045 | 2654 | 3048 | 2630 | 3685 | 2956 | 2824 | 3106 | 1674 | 2297 | 2412 | 2383
5 | 2395 | 2592 | 2882 | 2017 | 3921 | 2995 | 3048 | 2917 | 1677 | 2164 | 2396 | 2351
6 | 2856 | 2390 | 3119 | 3364 | 4368 | 2968 | 3694 | 2446 | 2309 | 2450 | 2904 | 2773
7 | 3559 | 2725 | 3348 | 3484 | 4511 | 3211 | 3812 | 2933 | 2357 | 3152 | 2944 | 3581
8 | 4659 | 3433 | 3242 | 3512 | 3686 | 3716 | 3714 | 4525 | 2761 | 3936 | 2888 | 3599
9 | 4119 | 2986 | 2896 | 2835 | 3412 | 3720 | 3631 | 3783 | 2625 | 3596 | 3583 | 3151
10 | 3693 | 3795 | 2505 | 3828 | 4865 | 3447 | 3650 | 3822 | 3239 | 2812 | 4155 | 3118
11 | 3205 | 4727 | 2493 | 4219 | 5753 | 3483 | 3176 | 3812 | 3766 | 3318 | 4299 | 2937
12 | 3387 | 4828 | 2523 | 4252 | 6121 | 3321 | 2777 | 3529 | 3923 | 3002 | 4364 | 3111
13 | 4197 | 4650 | 2518 | 4079 | 5424 | 2977 | 1997 | 2160 | 3471 | 2379 | 3522 | 2743
14 | 4053 | 4193 | 2592 | 4106 | 3709 | 3059 | 1919 | 2150 | 2004 | 3583 | 3365 | 3008
15 | 4179 | 2986 | 3366 | 4191 | 2976 | 2803 | 1987 | 2096 | 1696 | 3668 | 3359 | 2853
16 | 4407 | 3830 | 3254 | 3682 | 2559 | 2476 | 2264 | 2269 | 1670 | 3540 | 3823 | 2981
17 | 4501 | 4661 | 3106 | 3136 | 2611 | 4090 | 2473 | 2540 | 1886 | 3624 | 4053 | 2918
18 | 4718 | 5362 | 2672 | 2814 | 2652 | 4371 | 2740 | 3009 | 2210 | 3548 | 3970 | 3706
19 | 5088 | 5388 | 3072 | 2547 | 3547 | 4635 | 3082 | 3542 | 2370 | 2758 | 3379 | 4412
20 | 5004 | 4904 | 3247 | 2716 | 4455 | 4945 | 3455 | 3557 | 2413 | 3382 | 1954 | 4180
21 | 4194 | 4036 | 2780 | 2558 | 5607 | 4641 | 3443 | 3198 | 2380 | 3841 | 2134 | 3799
22 | 3978 | 4216 | 1787 | 2085 | 6096 | 5365 | 3049 | 2341 | 2132 | 3376 | 2431 | 3770
23 | 3694 | 3948 | 1686 | 1477 | 5650 | 5054 | 1839 | 2054 | 2143 | 2749 | 2437 | 3697
24 | 2250 | 3245 | 1223 | 1781 | 3362 | 4308 | 2163 | 1967 | 1946 | 2861 | 2301 | 3770
Total | 89721 | 88396 | 64618 | 72326 | 98797 | 85999 | 65790 | 68014 | 55998 | 73652 | 73866 | 77222

## 2026 ECRS
2026 ECRS
HE | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
1 | 1293 | 1083 | 794 | 831 | 1193 | 1127 | 1173 | 1316 | 1150 | 1138 | 1022 | 1480
2 | 1261 | 1026 | 1016 | 1027 | 1303 | 1050 | 1064 | 1241 | 1069 | 1005 | 969 | 933
3 | 1280 | 1021 | 981 | 1040 | 1154 | 1027 | 1069 | 1174 | 1051 | 1051 | 996 | 940
4 | 1268 | 1020 | 1011 | 975 | 1003 | 1002 | 1050 | 1129 | 1042 | 808 | 1000 | 914
5 | 1316 | 1054 | 1127 | 766 | 1074 | 1001 | 1026 | 1162 | 1044 | 985 | 1008 | 972
6 | 1472 | 1175 | 1215 | 1358 | 1360 | 1050 | 1310 | 1212 | 1083 | 1220 | 1350 | 1132
7 | 1646 | 1302 | 1466 | 1368 | 1458 | 1084 | 1440 | 1266 | 1171 | 1414 | 1419 | 1532
8 | 2085 | 1542 | 1615 | 1503 | 1868 | 2345 | 2365 | 2056 | 1341 | 1726 | 1428 | 1668
9 | 2794 | 2473 | 1958 | 2019 | 2844 | 2665 | 2643 | 3162 | 1804 | 2125 | 3078 | 2148
10 | 2854 | 3224 | 2092 | 2353 | 3124 | 2588 | 2610 | 3024 | 2708 | 2565 | 2797 | 2075
11 | 1779 | 2672 | 1558 | 2349 | 3257 | 2545 | 2343 | 2625 | 2713 | 2114 | 2423 | 1540
12 | 1490 | 2346 | 1559 | 2096 | 3571 | 2355 | 1973 | 2375 | 2634 | 1848 | 1859 | 1408
13 | 1739 | 2325 | 1417 | 2138 | 3521 | 2261 | 1834 | 1840 | 2615 | 1468 | 1609 | 1287
14 | 2270 | 2489 | 1364 | 2234 | 2498 | 2414 | 1691 | 1817 | 1752 | 2213 | 2046 | 1772
15 | 2672 | 2000 | 2124 | 2393 | 2350 | 2383 | 2000 | 1881 | 1683 | 2425 | 2088 | 1924
16 | 2570 | 2528 | 2402 | 2516 | 2213 | 1944 | 2120 | 2082 | 1620 | 2688 | 2471 | 1801
17 | 2408 | 2743 | 2304 | 2457 | 2350 | 3367 | 2470 | 2411 | 1727 | 2842 | 2491 | 1668
18 | 1883 | 2343 | 1827 | 1898 | 2490 | 3545 | 2395 | 2443 | 1768 | 2672 | 2302 | 1628
19 | 1683 | 2124 | 1612 | 1560 | 2528 | 3461 | 2278 | 2235 | 1823 | 1724 | 1485 | 1305
20 | 1562 | 1654 | 1264 | 1285 | 1986 | 2862 | 1953 | 2119 | 1919 | 1687 | 1272 | 1408
21 | 1513 | 1393 | 1233 | 1314 | 2421 | 2153 | 1893 | 2095 | 1788 | 1491 | 1200 | 1280
22 | 1486 | 1510 | 1032 | 1133 | 2422 | 1777 | 1696 | 1908 | 1607 | 1524 | 1130 | 1368
23 | 1459 | 1601 | 988 | 1032 | 2295 | 1733 | 1519 | 1678 | 1462 | 1228 | 1136 | 1379
24 | 1326 | 1166 | 833 | 872 | 1290 | 1497 | 1297 | 1462 | 1266 | 1169 | 1132 | 1495
Total | 43109 | 43814 | 34792 | 38517 | 51573 | 49236 | 43212 | 45713 | 39840 | 41130 | 39711 | 35057

## Reg - Adj Tables
Regulation Up and Down Wind Adjustment Tables
Incremental MW Adjustment, per 1000 MW of Incremental Wind Generation Capacity, to Account for Wind Capacity Growth
RegUp | Hour Ending
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Jan. | 2.0446 | 2.002 | 1.8515 | 1.906 | 1.7355 | 2.1239 | 1.9408 | 2.0305 | 2.8455 | 2.8607 | 2.0404 | 1.7288 | 1.7291 | 1.8761 | 2.2254 | 2.2372 | 2.3561 | 2.8943 | 1.7325 | 1.5544 | 1.693 | 1.551 | 1.7227 | 1.8798 | #REF!
Feb. | 1.9009 | 1.7638 | 1.8785 | 1.7807 | 2.0446 | 1.6892 | 1.9039 | 1.6522 | 3.1698 | 2.0008 | 1.8255 | 1.6607 | 1.6938 | 1.9795 | 2.1873 | 2.1302 | 2.1644 | 2.3423 | 1.8423 | 1.4936 | 1.5258 | 1.5451 | 1.5649 | 1.7179 | #REF!
Mar. | 2.022 | 1.9561 | 1.931 | 2.0604 | 1.8557 | 1.9467 | 1.6567 | 1.8004 | 2.8828 | 2.0022 | 2.173 | 2.0704 | 2.1125 | 1.9082 | 2.0979 | 1.9805 | 2.0721 | 2.3052 | 2.1 | 1.824 | 1.5835 | 1.7545 | 1.8629 | 1.9691 | #REF!
Apr. | 2.0613 | 2.1435 | 1.8683 | 1.9568 | 1.9712 | 1.8902 | 1.8511 | 1.993 | 3.0345 | 2.1466 | 2.247 | 2.1585 | 2.2401 | 2.2889 | 2.1722 | 2.4041 | 2.2203 | 2.262 | 2.4873 | 2.1805 | 2.1722 | 1.6644 | 1.7108 | 1.9316 | #REF!
May | 1.8794 | 2.0569 | 1.892 | 1.8133 | 1.812 | 1.8144 | 1.7032 | 2.1268 | 2.0841 | 1.4272 | 2.0684 | 1.5429 | 1.6028 | 1.6296 | 1.7871 | 1.8571 | 2.012 | 2.1043 | 2.0979 | 2.3657 | 1.9529 | 1.7884 | 2.1064 | 1.9454 | #REF!
Jun. | 1.0848 | 0.9542 | 1.0105 | 0.96877 | 0.96274 | 0.83145 | 1.0228 | 1.3358 | 0.89737 | 0.98155 | 1.0075 | 0.95783 | 0.85827 | 1.0237 | 0.79036 | 0.90471 | 0.89639 | 1.0916 | 1.1101 | 1.0802 | 0.9881 | 0.90098 | 1.0004 | 0.98775 | #REF!
Jul. | 0.80536 | 0.77848 | 0.81999 | 0.80563 | 0.74283 | 0.79886 | 0.81366 | 1.0537 | 0.85296 | 0.72546 | 0.81787 | 0.66108 | 0.66776 | 0.64902 | 0.77716 | 0.77405 | 0.89603 | 0.81439 | 0.83968 | 0.72379 | 0.74249 | 0.61802 | 0.69006 | 0.69509 | #REF!
Aug. | 0.8056 | 0.68953 | 0.689 | 0.7546 | 0.65214 | 0.72373 | 0.57523 | 0.72411 | 1.0859 | 0.67348 | 0.79059 | 0.6871 | 0.67841 | 0.67683 | 0.78862 | 0.78423 | 0.91751 | 0.90415 | 0.85964 | 0.87716 | 0.62047 | 0.60908 | 0.68617 | 0.65524 | #REF!
Sep. | 0.62513 | 0.67768 | 0.60449 | 0.69253 | 0.59305 | 0.61814 | 0.57602 | 0.60956 | 0.9605 | 0.56562 | 0.62793 | 0.65587 | 0.57642 | 0.62562 | 0.66297 | 0.60112 | 0.6296 | 0.7485 | 0.83414 | 0.52723 | 0.46981 | 0.52327 | 0.59687 | 0.59973 | #REF!
Oct. | 0.67836 | 0.68624 | 0.65644 | 0.75869 | 0.59956 | 0.69417 | 0.6477 | 0.62031 | 0.97671 | 1.2448 | 0.67581 | 0.74003 | 0.62408 | 0.6091 | 0.70279 | 0.71373 | 0.72239 | 0.75218 | 0.76974 | 0.3946 | 0.51773 | 0.54297 | 0.64911 | 0.6555 | #REF!
Nov. | 0.60563 | 0.65198 | 0.63459 | 0.55453 | 0.61552 | 0.567 | 0.53266 | 0.57609 | 0.82415 | 0.61093 | 0.49055 | 0.56297 | 0.54135 | 0.51031 | 0.52094 | 0.49686 | 0.59202 | 0.46965 | 0.33898 | 0.41937 | 0.46583 | 0.49375 | 0.46606 | 0.57037 | #REF!
Dec. | 2.1689 | 2.1067 | 2.1231 | 2.1824 | 2.0893 | 2.1452 | 2.2378 | 2.3827 | 3.2433 | 2.9549 | 1.751 | 2.0765 | 1.9267 | 1.8862 | 1.9482 | 2.2507 | 2.4458 | 1.8661 | 1.3615 | 1.3803 | 1.5622 | 2.1356 | 1.9956 | 2.2537 | #REF!
Incremental MW Adjustment, per 1000 MW of Incremental Wind Generation Capacity, to Account for Wind Capacity Growth
RegDown | Hour Ending
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Jan. | 1.7791 | 1.8722 | 1.8297 | 1.7808 | 1.9953 | 1.794 | 1.858 | 1.7596 | 1.7288 | 1.8379 | 1.8649 | 1.9533 | 1.8993 | 2.0356 | 2.0877 | 1.8673 | 1.8782 | 2.1107 | 2.1814 | 2.2616 | 1.9006 | 2.2577 | 2.1957 | 1.9996
Feb. | 1.5745 | 1.6933 | 1.6412 | 1.5037 | 1.681 | 1.66 | 1.636 | 1.5202 | 1.736 | 1.9624 | 1.7328 | 2.0124 | 2.3566 | 2.075 | 2.1324 | 2.0918 | 1.9481 | 1.7898 | 2.5658 | 2.6087 | 1.9051 | 2.0962 | 1.754 | 1.551
Mar. | 1.6638 | 1.788 | 1.5422 | 1.5256 | 1.5563 | 1.7217 | 1.4761 | 1.3844 | 1.905 | 2.1408 | 2.0474 | 1.8183 | 1.9528 | 1.8977 | 2.0799 | 2.0963 | 2.4194 | 2.4266 | 2.3726 | 2.7503 | 2.8026 | 2.3202 | 1.8824 | 1.7702
Apr. | 1.8931 | 1.8861 | 1.74 | 1.8144 | 1.6203 | 1.7311 | 1.7745 | 1.3568 | 2.0346 | 2.5398 | 1.9134 | 1.7698 | 1.6857 | 2.1674 | 2.2915 | 2.2749 | 2.539 | 2.6779 | 2.1665 | 2.8341 | 2.9341 | 2.6243 | 2.1568 | 1.9582
May | 1.9455 | 1.8066 | 1.5037 | 1.5243 | 1.7886 | 1.626 | 1.6571 | 1.3191 | 1.9654 | 1.7522 | 1.6425 | 1.5302 | 1.6107 | 1.8973 | 1.8847 | 1.9491 | 2.2248 | 2.7335 | 2.8052 | 2.2641 | 2.413 | 2.689 | 2.194 | 2.1825
Jun. | 1.161 | 0.90241 | 0.88722 | 0.87358 | 0.80743 | 0.78806 | 0.69434 | 0.85459 | 1.2372 | 0.89817 | 0.69898 | 0.81669 | 0.69258 | 0.96432 | 0.99209 | 1.0569 | 1.2777 | 1.2856 | 1.3509 | 1.3338 | 1.2825 | 1.2785 | 1.1592 | 1.0436
Jul. | 0.69339 | 0.58197 | 0.55646 | 0.52568 | 0.61144 | 0.52236 | 0.52036 | 0.34421 | 0.92239 | 0.56757 | 0.54185 | 0.57557 | 0.71231 | 0.76889 | 0.81515 | 0.88632 | 0.98339 | 0.98961 | 0.92485 | 1.0079 | 0.88342 | 1.1456 | 0.89657 | 0.72584
Aug. | 0.61226 | 0.54594 | 0.5452 | 0.48516 | 0.49638 | 0.53295 | 0.43239 | 0.38447 | 0.79449 | 0.51708 | 0.46803 | 0.56373 | 0.59138 | 0.79655 | 0.83842 | 0.89686 | 1.0772 | 1.0407 | 1.2236 | 0.97577 | 1.0687 | 1.0962 | 0.84636 | 0.67485
Sep. | 0.52784 | 0.48266 | 0.42557 | 0.4745 | 0.45461 | 0.45413 | 0.4253 | 0.35316 | 0.51725 | 0.72523 | 0.43485 | 0.43256 | 0.51011 | 0.52285 | 0.72036 | 0.7208 | 0.75119 | 0.76461 | 0.71316 | 0.82737 | 1.1848 | 0.85123 | 0.70712 | 0.56757
Oct. | 0.51469 | 0.44724 | 0.51748 | 0.39619 | 0.51218 | 0.45964 | 0.50584 | 0.45837 | 0.43628 | 0.75451 | 0.64524 | 0.56085 | 0.48377 | 0.6291 | 0.64658 | 0.71677 | 0.67294 | 0.71049 | 0.63891 | 0.99527 | 1.0142 | 0.63808 | 0.60179 | 0.56558
Nov. | 0.30889 | 0.35445 | 0.35197 | 0.34191 | 0.28899 | 0.3687 | 0.33693 | 0.28977 | 0.38495 | 0.38441 | 0.3958 | 0.36756 | 0.46268 | 0.45003 | 0.37127 | 0.38411 | 0.36284 | 0.54337 | 0.62279 | 0.60218 | 0.49165 | 0.42803 | 0.36051 | 0.38567
Dec. | 1.5569 | 1.2974 | 1.4669 | 1.5053 | 1.3867 | 1.4944 | 1.3801 | 1.6444 | 1.2097 | 1.8073 | 1.8931 | 1.7009 | 1.7945 | 1.7318 | 1.418 | 1.4969 | 1.3982 | 1.9372 | 2.2791 | 1.9116 | 1.6485 | 1.6389 | 1.8154 | 1.4757
Regulation Up and Down Solar Adjustment Tables
Incremental MW Adjustment, per 1000 MW of Incremental Solar Generation Capacity, to Account for Solar Capacity Growth
RegUp | Hour Ending
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Jan. | 0 | 0 | 0 | 0 | 0 | 0 | 1.2283 | 18.1743 | 10.1508 | 34.4042 | 24.7302 | 20.3006 | 21.5337 | 25.9429 | 30.2762 | 31.9318 | 48.3751 | 39.4858 | 17.3957 | 0.32419 | 0.26013 | 0.24689 | 0 | 0
Feb. | 0 | 0 | 0 | 0 | 0 | 0 | 4.952 | 19.8227 | 29.4322 | 42.4483 | 33.6886 | 28.3542 | 35.5213 | 37.9487 | 42.0111 | 43.4185 | 43.511 | 63.2519 | 16.07 | 5.4179 | 3.0276 | 3.1469 | 0 | 0
Mar. | 0 | 0 | 0 | 0 | 0 | 0 | 1.8018 | 18.2286 | 20.1618 | 44.1867 | 40.1791 | 41.8367 | 38.9159 | 40.875 | 42.5645 | 51.5218 | 47.884 | 64.9734 | 60.396 | 28.0266 | 1.9465 | 0.19867 | 0 | 0
Apr. | 0 | 0 | 0 | 0 | 0 | 0 | 7.5793 | 17.8183 | 22.7271 | 41.3048 | 32.9302 | 33.3267 | 38.3412 | 40.0247 | 39.7372 | 43.7011 | 50.1931 | 43.4764 | 54.2263 | 44.3694 | 20.2014 | 1.5764 | 0 | 0
May | 0 | 0 | 0 | 0 | 0 | 0 | 19.3838 | 15.454 | 33.2577 | 40.6946 | 38.5306 | 39.9315 | 43.445 | 44.554 | 37.9447 | 45.1017 | 53.1226 | 48.7803 | 39.1676 | 41.4389 | 14.1761 | 0.35049 | 0 | 0
Jun. | 0 | 0 | 0 | 0 | 0 | 0 | 24.6699 | 12.6874 | 37.6786 | 45.9852 | 36.9493 | 39.3018 | 31.6128 | 39.1731 | 35.2568 | 32.8939 | 40.7298 | 45.4136 | 37.8815 | 55.353 | 29.3201 | 1.4311 | 0 | 0
Jul. | 0 | 0 | 0 | 0 | 0 | 0 | 27.909 | 17.7012 | 38.7562 | 45.2731 | 34.828 | 35.4496 | 35.2114 | 31.3463 | 36.9074 | 37.5332 | 43.895 | 42.5659 | 35.5962 | 47.9608 | 15.3143 | 1.2082 | 0 | 0
Aug. | 0 | 0 | 0 | 0 | 0 | 0 | 16.6531 | 22.734 | 26.1468 | 37.1102 | 24.3215 | 24.5995 | 23.2145 | 28.0724 | 30.9084 | 35.1043 | 33.0772 | 37.8389 | 38.9307 | 40.7079 | 9.6154 | 0.34275 | 0 | 0
Sep. | 0 | 0 | 0 | 0 | 0 | 0 | 1.5718 | 20.3667 | 30.8627 | 36.0275 | 26.0824 | 28.9341 | 35.1204 | 29.6352 | 34.8761 | 39.0417 | 41.5159 | 46.9135 | 37.2154 | 15.0977 | 5.5536 | 0.48039 | 0 | 0
Oct. | 0 | 0 | 0 | 0 | 0 | 0 | 0.29372 | 8.9535 | 16.2521 | 24.4222 | 19.7664 | 19.9976 | 23.6881 | 24.1617 | 22.3108 | 25.1408 | 30.6796 | 41.8433 | 25.1367 | 2.1291 | 0.5491 | 0.23947 | 0 | 0
Nov. | 0 | 0 | 0 | 0 | 0 | 0 | 2.4151 | 22.2959 | 32.0572 | 30.3612 | 26.5672 | 21.7767 | 28.9091 | 31.5043 | 34.9176 | 42.0621 | 53.8119 | 16.451 | 9.9717 | 0.38072 | 0.15325 | 0.077569 | 0 | 0
Dec. | 0 | 0 | 0 | 0 | 0 | 0 | 1.3612 | 21.0143 | 17.4248 | 31.7968 | 22.3362 | 23.163 | 25.8117 | 30.0212 | 34.6792 | 37.7838 | 45.8108 | 13.2448 | 6.7875 | 0.25786 | 0.12431 | 0.11315 | 0 | 0
Incremental MW Adjustment, per 1000 MW of Incremental Solar Generation Capacity, to Account for Solar Capacity Growth
RegDown | Hour Ending
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Jan. | 0 | 0 | 0 | 0 | 0 | 0 | 0.11645 | 7.6447 | 62.8686 | 29.87 | 23.2728 | 19.0725 | 20.8143 | 24.8077 | 27.6462 | 32.95 | 21.1031 | 15.0168 | 16.6652 | 0.11945 | 0.39021 | 0.26434 | 0 | 0
Feb. | 0 | 0 | 0 | 0 | 0 | 0 | 3.5259 | 40.8529 | 82.3995 | 30.3047 | 29.4287 | 29.6216 | 32.8052 | 34.3468 | 37.8581 | 38.4148 | 40.5993 | 14.6708 | 27.0042 | 2.1106 | 0.1444 | 3.118 | 0 | 0
Mar. | 0 | 0 | 0 | 0 | 0 | 0 | 0.3477 | 26.9173 | 56.9705 | 39.2814 | 37.6725 | 41.8107 | 33.1131 | 45.0456 | 40.6227 | 45.6441 | 45.8047 | 50.9537 | 26.3331 | 13.5664 | 8.438 | 0.066665 | 0 | 0
Apr. | 0 | 0 | 0 | 0 | 0 | 0 | 0.56355 | 37.2842 | 65.8468 | 27.1546 | 32.128 | 36.2785 | 34.3331 | 36.2166 | 38.0292 | 34.9384 | 38.9573 | 51.1611 | 38.355 | 14.6884 | 24.2097 | 0.59441 | 0 | 0
May | 0 | 0 | 0 | 0 | 0 | 0 | 3.1205 | 36.5809 | 45.2324 | 34.9725 | 34.0475 | 40.0475 | 35.694 | 35.8866 | 43.0956 | 42.2933 | 45.4199 | 42.889 | 31.7887 | 14.7206 | 23.6592 | 4.4938 | 0 | 0
Jun. | 0 | 0 | 0 | 0 | 0 | 0 | 7.5367 | 52.7483 | 36.792 | 31.0747 | 34.197 | 35.5572 | 39.403 | 33.8956 | 39.6251 | 39.895 | 44.5698 | 43.3953 | 43.1087 | 20.0491 | 28.3278 | 15.4149 | 0 | 0
Jul. | 0 | 0 | 0 | 0 | 0 | 0 | 6.9485 | 40.5715 | 39.2015 | 29.6376 | 25.707 | 26.76 | 30.4358 | 34.1062 | 34.0553 | 39.678 | 40.5862 | 41.1959 | 34.4334 | 14.5338 | 30.5182 | 13.7632 | 0 | 0
Aug. | 0 | 0 | 0 | 0 | 0 | 0 | 17.4601 | 42.4235 | 60.8902 | 23.2282 | 21.5026 | 19.0452 | 27.9766 | 32.1138 | 33.417 | 37.8092 | 32.8109 | 41.5019 | 30.5635 | 9.922 | 32.9376 | 1.1323 | 0 | 0
Sep. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.1733 | 50.4339 | 32.171 | 31.821 | 30.9792 | 30.7413 | 27.9233 | 33.6565 | 30.4347 | 32.4895 | 34.1605 | 23.8847 | 12.4349 | 3.5418 | 0.45509 | 0 | 0
Oct. | 0 | 0 | 0 | 0 | 0 | 0 | 0.16331 | 6.2987 | 40.1077 | 26.7694 | 21.851 | 22.3436 | 24.073 | 24.7517 | 19.514 | 27.7101 | 26.7417 | 26.7964 | 8.2582 | 7.5099 | 0.47161 | 0.23056 | 0 | 0
Nov. | 0 | 0 | 0 | 0 | 0 | 0 | 1.1361 | 22.6262 | 44.0468 | 35.3679 | 30.0822 | 32.5245 | 27.6634 | 22.068 | 25.1691 | 30.4397 | 18.9122 | 8.5325 | 1.9762 | 0.12169 | 0.1632 | 0.16601 | 0 | 0
Dec. | 0 | 0 | 0 | 0 | 0 | 0 | 0.22443 | 18.4703 | 59.3632 | 42.4323 | 30.8616 | 29.8886 | 27.5064 | 24.5172 | 24.6125 | 33.6157 | 15.2701 | 14.5366 | 3.239 | 0.14476 | 0.11321 | 0.11608 | 0 | 0