ERCOT Nodal Operating Guides

Section 7:  Telemetry and Communication

June 1, 2022

7	Telemetry and Communication	1

7.1	ERCOT Wide Area Network	1

7.1.1	ERCOT Responsibilities	2

7.1.2	WAN Participant Responsibilities	2

7.1.3	Joint Responsibilities (Maintenance and Restoration)	10

7.2	ERCOT ICCP Interface	11

7.2.1	Quality Codes	11

7.2.2	Metric of Availability	11

7.3	Telemetry	12

7.3.1	Data from ERCOT to QSEs	13

7.3.2	Data from ERCOT to TSP	13

7.3.3	Data from WAN Participants to ERCOT	14

7.3.4	Resolving Real-Time Data Issues that affect ERCOT Network Security Analysis	15

7.3.5	TSP and QSE Telemetry Restoration	16

7.3.6	General Telemetry Performance Criterion	16

7.4	Calibration and Testing of Telemetry Responsibilities	16

7.5	Competitive Renewable Energy Zone Circuits and Stations	16

# 7	Telemetry and Communication

- 7.1	ERCOT Wide Area Network

(1)	ERCOT interfaces with Wide Area Network (WAN) Participants over the WAN.  ERCOT is responsible for the design, configuration, maintenance, and management of the communications network infrastructure required to support WAN connectivity.  This includes, but is not limited to, ERCOT issued routers, switches, and out-of-band management equipment.  The ERCOT WAN is a redundant, highly available network providing connectivity to ERCOT sites and each Market Participant site.  See Figure 1, ERCOT Wide Area Network Overview, in Section 7.1.2, WAN Participant Responsibilities.

(2)	The primary purpose of the ERCOT WAN is to facilitate Transmission Control Protocol/Internet Protocol (TCP/IP) connectivity between ERCOT and WAN Participants for exchange of:

(a)	Inter-Control Center Communications Protocol (ICCP) Data, including but not limited to Real-Time telemetry data for wholesale operations, frequency control, and transmission security; and

(b)	Applications Programming Interface (API) data, including but not limited to, Resource-Specific Extensible Markup Language (XML) Data, such as market operations, operating plans, Outage requests, or Dispatch instructions.

(3)       The ERCOT WAN is also used to facilitate dedicated voice communication between ERCOT and Market Participants.

(4)	Data exchanged between ERCOT and WAN Participants shall use the ERCOT WAN for the following types of data:

(a)	ICCP Data;

(b)	Resource-Specific XML Data; and

(c)	Operational voice communications for both normal and emergency use.  The ERCOT WAN includes support for, but not limited to, off-premise exchanges (OPX) with ERCOT’s control facilities and the ERCOT Hotlines.

(5)	ERCOT may approve conditional use of other forms of data exchange or communications for exchange of the types of data listed in paragraph (4) above when a WAN Participant loses their connection to the ERCOT WAN.  A WAN Participant may use the Internet as a tertiary communication path if the ERCOT WAN and backup communication paths are both unavailable.

(6)	WAN Participants shall sign the ERCOT Private WAN Agreement in the current form required by ERCOT as a condition to be granted access to the WAN.

(7)	A Qualified Scheduling Entity (QSE) representing a Resource or a QSE representing an Emergency Response Service (ERS) Resource may designate another QSE (including a Data Agent-Only QSE, as provided in ERCOT Protocol Section 16.2.1.1, Data Agent-Only Qualified Scheduling Entities) as its agent for purposes of exchanging over the ERCOT WAN one or more of the types of data listed in paragraph (4) above.  Such designation shall be made using the QSE Agency Agreement form.

[NOGRR239: Insert paragraph (8) below on July 1, 2022:] (8) ERCOT shall provide encryption and manage the related encryption keys for data transmitted between ERCOT and each ERCOT-managed router at each WAN Participant’s WAN demarcation point. QSEs and Transmission Operators (TOs) are responsible for providing security protection of data transmitted downstream from the ERCOT-managed router.

- 7.1.1	ERCOT Responsibilities

(1)	ERCOT’s responsibilities include the following:

(a)	Supply Customer Premises equipment (i.e. equipment at WAN Participant facilities for the WAN) including routers, Local Area Network (LAN) switch/hub and all support equipment for management purposes;

(b)	Order and provision of local loop, network access point and transport;

(c)  	Complete required coordinated WAN qualification testing and approval for service;

(d)	Provide 24-hour network monitoring and management;

(e)	Provide 24x7 maintenance, with 4-hour response, for all ERCOT equipment located at WAN Participant site; and

(f)	The ERCOT Helpdesk will be the single point of contact for all network issues, and the ERCOT Helpdesk will provide periodic updates to the WAN Participant until the issue is resolved.

### 7.1.2	WAN Participant Responsibilities

(1)	WAN Participant responsibilities include the following:

(a)	A prospective WAN Participant is required to complete a WAN application, signed by the WAN Participant’s Authorized Representative, and sign the ERCOT Private WAN Agreement, which governs installation, operation, and maintenance of the WAN hardware.  Appropriate WAN documents can be obtained by contacting ERCOT.  The WAN application shall include the following information at a minimum:

(i)  	WAN circuit termination location and requested functionality specifications;

(ii) 	WAN Participant’s primary and backup contacts for WAN facilities management and services;

(iii)  	WAN Participant’s primary and backup contacts for WAN emergency restoration;

(iv)	WAN Invoicing contact information;

(v)	WAN Participant’s 24x7 operations desk long distance number; and

(vi)	WAN Participant’s 24x7 analog line for maintenance.

(b)	Each WAN Participant must timely update information provided to ERCOT in the application process, and must promptly respond to any reasonable request by ERCOT for updated information regarding the WAN Participant or the information provided to ERCOT in item (a) above.  Changes to any of the information listed in item (a) above shall be submitted to ERCOT using a Notice of Change of Information (NCI) form.

(c)	A WAN Participant shall provide physical security systems compliant with the applicable Critical Infrastructure Protection (CIP) requirement of the North American Electric Reliability Corporation (NERC) Reliability Standards.

(d)	WAN Participant equipment provided by ERCOT that exchanges ICCP Data, Resource-Specific XML Data, or operational voice communications with ERCOT shall connect directly to the ERCOT WAN.  ERCOT will work with each WAN Participant to determine the most appropriate WAN demarcation point.  Criteria for determining demarcation points include:

(i)	Reliability;

(ii)	Location of data centers;

(iii)	Location of control centers and/or communication centers;

(iv)	Location of disaster recovery facilities;

(v)	Location of Energy and Market Management System (EMMS) equipment;

(vi)	Location of ICCP equipment;

(vii)	Location of Resource-Specific XML equipment; and

(viii)	Location of private branch exchange (PBX) or call management equipment installation.

(e)	ERCOT is responsible for designating necessary WAN equipment for the reliable transport of communications over the ERCOT WAN and will make the ultimate determination of the demarcation point location.

(f)	A WAN Participant that serves both Transmission Service Provider (TSP) and QSE functions at one location may have a single ERCOT WAN connection as defined in Section 7.1, ERCOT Wide Area Network, at that location.

(g)	If a TSP and QSE share a centralized PBX or call management, separate OPX circuits will be terminated for each participant.

(h)	Each WAN Participant is required to extend the ERCOT OPX and Hotline voice circuits into its 24x7 operations desk.  The OPX and Hotline voice circuits are transported across the ERCOT WAN.  If a WAN Participant is designated to represent another Market Participant through an agency agreement approved by ERCOT, the WAN Participant must have dedicated OPX circuits for each Market Participant represented, in addition to a dedicated OPX for the WAN Participant if it is also representing Resources.  In these cases, a single Hotline button will be used for the WAN Participant and all of the represented Market Participants.  The Market Participant and its agent, if applicable, are both responsible for delivering the Hotline and the OPX to the Market Participant’s 24x7 operations desk in a manner that reasonably assures continuous communication with ERCOT and is not affected by calling features such as automatic transfer or roll to voice mail.  Also, a touchtone keypad is required for the Hotline to be able to provide an acknowledged receipt.  The demarcation point for all voice circuits is the WAN Participant’s router.

(i)	Each WAN Participant must provide internal facilities and communications to collect and furnish data and voice signals to the ERCOT WAN as required by the Protocols.  For TSPs and Transmission Operators (TOs) such data includes, but is not limited to, voice communications, ICCP Data, and Supervisory Control and Data Acquisition (SCADA) for substations and other Transmission Facilities.  For QSEs such data includes, but is not limited to, operational voice communications, ICCP Data, Resource-Specific XML Data, and SCADA for Resources.

(j)	A WAN Participant shall provide adequate physical facilities to support the ERCOT WAN communications equipment.  The physical facilities and communications equipment requirements include the following:

(i)	Provide an analog business phone line or PBX analog extension for troubleshooting and maintenance of equipment;

(ii)	Provide a height of 24” of rack space in a 19” wide rack;

(iii)	Provide two separate uninterruptible power supply single-phase 115 VAC 20 amp circuits, each with four receptacles in the 19” rack listed above;

(iv)	Provide building wiring from circuit termination to equipment rack;

(v)	Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility;

(vi)	Within one-hour notice, provide ERCOT employees or contractors emergency access to the communication facility;

(vii)	Provide onsite personnel to escort ERCOT employees or contractors;

(viii)	Provide a firewall or router, located at the WAN Participant site, for the network address translation of internal WAN Participant addresses to external addresses on the ERCOT LAN;

(ix)	Provide connectivity from WAN Participant firewall or router to ERCOT LAN located at WAN Participant site.  WAN Participants are responsible for their own security through this connection;

(x)	Dual cable entrances to WAN Participant, connecting to different Telco Central Offices are highly recommended; and

(xi)	Provide ERCOT with internal IP addressing scheme as needed for network design.  This will be kept confidential.

(k)	A WAN Participant shall supply, implement, and maintain all data and voice communication facilities required to fulfill the obligations set forth in these Operating Guides.

(l)	A WAN Participant’s installation of data and voice communication facilities described in paragraph (k) above must complete qualification testing as specified by ERCOT before ERCOT will grant approval to commence operational use of the WAN connection.  A WAN Participant shall request prior approval from ERCOT of any changes in data and voice communication facilities that impact connectivity through the WAN and shall coordinate with ERCOT before commencing operational use.

(m)	If a WAN Participant: i) transmits or exchanges ICCP Data or Resource-Specific XML Data with another WAN Participant, or ii) extends its network or otherwise transmits ICCP Data, Resource-Specific XML Data, or operational voice communications to another of its control and/or data center or another WAN Participant’s control and/or data center, then such communications shall only be exchanged using a secure private network.  Examples of a secure private network would include, but would not be limited to, dedicated connections such as Multi-Protocol Label Switching (MPLS), Time Division Multiplexing Digital Signal 1 (TDM DS1), and Metro Ethernet.  This requirement does not apply to communications directly between the physical Resource location and a WAN Participant location.

INCLUDEPICTURE  "cid:image001.png@01D4C84F.EABE7930" \* MERGEFORMATINET  INCLUDEPICTURE  "cid:image001.png@01D4C84F.EABE7930" \* MERGEFORMATINET  INCLUDEPICTURE  "cid:image001.png@01D4C84F.EABE7930" \* MERGEFORMATINET

Figure 1 ERCOT Wide Area Network Overview

[NOGRR177: Replace Section 7.1.2 above with the following upon system implementation of NPRR857:] - 7.1.2 WAN Participant Responsibilities (1) WAN Participant responsibilities include the following: (a) A prospective WAN Participant is required to complete a WAN application, signed by the WAN Participant’s Authorized Representative, and sign the ERCOT Private WAN Agreement, which governs installation, operation, and maintenance of the WAN hardware. Appropriate WAN documents can be obtained by contacting ERCOT. The WAN application shall include the following information at a minimum: (i) WAN circuit termination location and requested functionality specifications; (ii) WAN Participant’s primary and backup contacts for WAN facilities management and services; (iii) WAN Participant’s primary and backup contacts for WAN emergency restoration; (iv) WAN Invoicing contact information; (v) WAN Participant’s 24x7 operations desk long distance number; and (vi) WAN Participant’s 24x7 analog line for maintenance. (b) Each WAN Participant must timely update information provided to ERCOT in the application process, and must promptly respond to any reasonable request by ERCOT for updated information regarding the WAN Participant or the information provided to ERCOT in item (a) above. Changes to any of the information listed in item (a) above shall be submitted to ERCOT using a Notice of Change of Information (NCI) form. (c) A WAN Participant shall provide physical security systems compliant with the applicable Critical Infrastructure Protection (CIP) requirement of the North American Electric Reliability Corporation (NERC) Reliability Standards. (d) WAN Participant equipment provided by ERCOT that exchanges ICCP Data, Resource-Specific XML Data, or operational voice communications with ERCOT shall connect directly to the ERCOT WAN. ERCOT will work with each WAN Participant to determine the most appropriate WAN demarcation point. Criteria for determining demarcation points include: (i) Reliability; (ii) Location of data centers; (iii) Location of control centers and/or communication centers; (iv) Location of disaster recovery facilities; (v) Location of Energy and Market Management System (EMMS) equipment; (vi) Location of ICCP equipment; (vii) Location of Resource-Specific XML equipment; and (viii) Location of private branch exchange (PBX) or call management equipment installation. (e) ERCOT is responsible for the reliable transport of communications over the ERCOT WAN and will make the ultimate determination of the demarcation point location. (f) A WAN Participant that serves both Transmission Operator (TO) and QSE functions at one location may have a single ERCOT WAN connection as defined in Section 7.1, ERCOT Wide Area Network, at that location. (g) If a TO and QSE share a centralized PBX or call management with a QSE, the QSE’s OPX circuits will be terminated separately from the OPX circuits of the TO. (h) Each WAN Participant is required to extend the ERCOT OPX and Hotline voice circuits into its 24x7 operations desk. The OPX and Hotline voice circuits are transported across the ERCOT WAN. If a WAN Participant is designated to represent another Market Participant through an agency agreement approved by ERCOT, the WAN Participant must have dedicated OPX circuits for each Market Participant represented, in addition to a dedicated OPX for the WAN Participant if it is also representing Resources. In these cases, a single Hotline button will be used for the WAN Participant and all of the represented Market Participants. The Market Participant and its agent, if applicable, are both responsible for delivering the Hotline and the OPX to the Market Participant’s 24x7 operations desk in a manner that reasonably assures continuous communication with ERCOT and is not affected by calling features such as automatic transfer or roll to voice mail. Also, a touchtone keypad is required for the Hotline to be able to provide an acknowledged receipt. The demarcation point for all voice circuits is the WAN Participant’s router. (i) Each WAN Participant must provide internal facilities and communications to collect and furnish data and voice signals to the ERCOT WAN as required by the Protocols. For TOs such data includes, but is not limited to, operational voice communications, ICCP Data, and Supervisory Control and Data Acquisition (SCADA) for substations and other Transmission Facilities. For QSEs, such data includes, but is not limited to, operational voice communications, ICCP Data, Resource-Specific XML Data, and SCADA for Resources. (j) A WAN Participant shall provide adequate physical facilities to support the ERCOT WAN communications equipment. The physical facilities and communications equipment requirements include the following: (i) Provide an analog business phone line or PBX analog extension for troubleshooting and maintenance of equipment; (ii) Provide a height of 24” of rack space in a 19” wide rack; (iii) Provide two separate uninterruptible power supply single-phase 115 VAC 20 amp circuits, each with four receptacles in the 19” rack listed above; (iv) Provide building wiring from circuit termination to equipment rack; (v) Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility; (vi) Within one-hour notice, provide ERCOT employees or contractors emergency access to the communication facility; (vii) Provide onsite personnel to escort ERCOT employees or contractors; (viii) Provide a firewall or router, located at the WAN Participant site, for the network address translation of internal WAN Participant addresses to external addresses on the ERCOT LAN; (ix) Provide connectivity from WAN Participant firewall or router to ERCOT LAN located at WAN Participant site. WAN Participants are responsible for their own security through this connection; (x) Dual cable entrances to WAN Participant, connecting to different Telco Central Offices are highly recommended; and (xi) Provide ERCOT with internal IP addressing scheme as needed for network design. This will be kept confidential. (k) A WAN Participant shall supply, implement, and maintain all data and voice communication facilities required to fulfill the obligations set forth in these Operating Guides. (l) A WAN Participant’s installation of data and voice communication facilities described in paragraph (k) above must complete qualification testing as specified by ERCOT before ERCOT will grant approval to commence operational use of the WAN connection. A WAN Participant shall request prior approval from ERCOT of any changes in data and voice communication facilities that impact connectivity through the WAN and shall coordinate with ERCOT before commencing operational use. (m) If a WAN Participant: i) transmits or exchanges ICCP Data or Resource-Specific XML Data with another WAN Participant, or ii) extends its network or otherwise transmits ICCP Data, Resource-Specific XML Data, or operational voice communications to another of its control and/or data center or another WAN Participant’s control and/or data center, then such communications shall only be exchanged using a secure private network. Examples of a secure private network would include, but would not be limited to, dedicated connections such as MPLS, Time Division Multiplexing Digital Signal 1 (TDM DS1), and Metro Ethernet. This requirement does not apply to communications directly between the physical Resource location and a WAN Participant location. INCLUDEPICTURE "cid:image001.png@01D4C84F.EABE7930" \* MERGEFORMATINET INCLUDEPICTURE "cid:image001.png@01D4C84F.EABE7930" \* MERGEFORMATINET INCLUDEPICTURE "cid:image001.png@01D4C84F.EABE7930" \* MERGEFORMATINET Figure 1 ERCOT Wide Area Network Overview

- 7.1.3	Joint Responsibilities (Maintenance and Restoration)

(1)	Joint responsibility of WAN Participants and ERCOT include the following:

(a)	Coordinate maintenance and restoration activities so its reliability is not compromised;

(b)	All primary and back-up circuits shall be tested annually or as otherwise requested by ERCOT for end-to-end performance;

(c)	ERCOT will specify test procedures for hotline and any back-up or alternate path voice circuits;

(d)	A WAN Participant shall troubleshoot WAN connectivity or performance as directed by ERCOT;

(e)        If WAN performance issues arise, a Market Participant shall take action to isolate circuit and equipment problems for quick resolution and restoration of service; and

(f)	Scheduled maintenance of any WAN hardware/software shall be coordinated between ERCOT and the affected WAN Participant.  The WAN Participant shall provide reasonable outage windows for ERCOT support personnel to upgrade and repair equipment and shall coordinate with ERCOT before commencing operational use.

## 7.2	ERCOT ICCP Interface

(1)	The Inter-Control Center Communications Protocol (ICCP) over the ERCOT Wide Area Network (WAN) provides the Real-Time telemetry data from Market Participant computers, computer networks, or other devices.  Market Participants providing the data using an ICCP link must format their data and coordinate installation according to the ERCOT WAN Agreement found in the ERCOT Nodal ICCP Communication Handbook. The ERCOT Nodal ICCP Communication Handbook provides additional details and shall be used in conjunction with the Protocols and Operating Guides to facilitate the communication needs of ERCOT and Market Participants to effectively manage system and market requirements.  Updates to the ERCOT Nodal ICCP Communication Handbook shall be approved by the Technical Advisory Committee (TAC).

### 7.2.1	Quality Codes

(1)	Status and analog telemetry data provided to ERCOT shall have the associated quality codes and associated attributes found in the ERCOT Nodal ICCP Communication Handbook.  ICCP quality codes to be provided to ERCOT by the Market Participant and to the Market Participants by ERCOT shall follow the standards set in the ERCOT Nodal ICCP Communication Handbook.

### 7.2.2	Metric of Availability

(1)	ICCP links must achieve availability as required by the Protocols.  Availability metrics shall establish a process to coordinate downtime for ICCP links and database maintenance.

(2)	ICCP links shall use fully redundant data communication from the Qualified Scheduling Entity (QSE) and Transmission Service Provider (TSP) control systems to the ERCOT System as required by the Protocols.

[NOGRR177: Replace paragraph (2) above with the following upon system implementation of NPRR857:] (2) ICCP links shall use fully redundant data communication from the WAN Participant control systems to the ERCOT System as required by the Protocols.

## 7.3	Telemetry

(1)	Qualified Scheduling Entities (QSEs) and Transmission Service Providers (TSPs) required to supply Real-Time telemetry data to ERCOT shall use an Inter-Control Center Communications Protocol (ICCP) interface through the ERCOT Wide Area Network (WAN).  TSPs and QSEs shall also receive signals from ERCOT over the ICCP interface.

(2)	Each QSE and TSP shall continuously provide to ERCOT the telemetry data quantities that they are responsible for in the format described in the ERCOT Nodal ICCP Communication Handbook.  The frequency of updates, means of communication to ERCOT, and data format for each point provided by each Entity shall follow the specifications in the ERCOT Nodal ICCP Communication Handbook.  At the frequency specified, each update cycle shall provide current operating data for all points being monitored.  Design accuracy and availability of data points delivered to ERCOT shall satisfy the requirements of the Protocols pursuant to Protocol Section 3.10.7.5, Telemetry Requirements.

(3)	QSEs, Resources and TSPs are required to provide power operation data to ERCOT according to the Protocols and the ERCOT Nodal ICCP Communication Handbook.

(4)	The nomenclature format of data (i.e. structure of the ICCP Object Name) shall follow the standards in the ERCOT Nodal ICCP Communication Handbook.

[NOGRR177: Replace Section 7.3 above with the following upon system implementation of NPRR857:] (1) WAN Participants required to supply Real-Time telemetry data to ERCOT shall use an Inter-Control Center Communications Protocol (ICCP) interface through the ERCOT Wide Area Network (WAN). WAN Participants shall also receive signals from ERCOT over the ICCP interface. (2) Each WAN Participant shall continuously provide to ERCOT the telemetry data quantities that they are responsible for in the format described in the ERCOT Nodal ICCP Communication Handbook. The frequency of updates, means of communication to ERCOT, and data format for each point provided by each Entity shall follow the specifications in the ERCOT Nodal ICCP Communication Handbook. At the frequency specified, each update cycle shall provide current operating data for all points being monitored. Design accuracy and availability of data points delivered to ERCOT shall satisfy the requirements of the Protocols pursuant to Protocol Section 3.10.7.5, Telemetry Requirements. (3) WAN Participants are required to provide power operation data to ERCOT according to the Protocols and the ERCOT Nodal ICCP Communication Handbook. (4) The nomenclature format of data (i.e. structure of the ICCP Object Name) shall follow the standards in the ERCOT Nodal ICCP Communication Handbook.

- 7.3.1	Data from ERCOT to QSEs

(1)	ERCOT shall provide all required data and issue instructions over the ERCOT WAN to QSEs in accordance with the Protocols and the ERCOT Nodal ICCP Communication Handbook.

(2)	ERCOT shall follow data requirements and standards described in the ERCOT Nodal ICCP Communication Handbook.

### 7.3.2	Data from ERCOT to TSP

(1)	ERCOT shall provide operational data over the ERCOT WAN to the TSP in accordance with the Protocols and the ERCOT Nodal ICCP Communication Handbook.

(2)	ERCOT is required to provide operational data to TSPs for the purpose of providing reliability information on current conditions.  TSPs may request QSE supplied data as allowed by the Protocols.

(3)	ERCOT will post notice to WAN Participants of all available data.

[NOGRR177: Replace applicable portions of Section 7.3.2 above with the following upon system implementation of NPRR857:] - 7.3.2 Data from ERCOT to TSPs and DCTOs (1) ERCOT shall provide operational data over the ERCOT WAN to TSPs and DCTOs in accordance with the Protocols and the ERCOT Nodal ICCP Communication Handbook. (2) ERCOT is required to provide operational data to TSPs and DCTOs for the purpose of providing reliability information on current conditions. TSPs may request QSE supplied data as allowed by the Protocols. (3) ERCOT will post notice to WAN Participants of all available data.

### 7.3.3	Data from WAN Participants to ERCOT

(1)	Each WAN Participant shall provide telemetered measurements over the ERCOT WAN on modeled Transmission Elements as required by the Protocols and the ERCOT Nodal ICCP Communication Handbook.

(2)	WAN Participants shall provide Real-Time monitoring of power system quantities to ERCOT as defined in the Protocols and the ERCOT Nodal ICCP Communication Handbook.  ERCOT shall work with WAN Participants to determine the required data using the methodology presented in the Protocols.  Transmission Element status and analog measurements that the TSPs and QSEs define in the Network Operations Model shall, at a minimum, be provided to ERCOT.  Ultimately, it is the responsibility of the TSPs and QSEs to provide all data requested by ERCOT.

(3)	Real-Time telemetry data from QSEs used to supply power or Ancillary Services shall be integrated by ERCOT and checked against settlement meter values on a monthly basis.

(4)	Each QSE and Transmission Operator (TO) shall notify ERCOT as soon as practicable when there are known telemetry data issues (telemetry data will not be available or is unreliable for operational purposes).  Each QSE or TO shall address the known telemetry data issue with either a correction of the telemetry data as soon as practicable, or a manual data replacement, if available, as soon as practicable.  The report, as outlined in Section 9.2.2, Real-Time Data Monitor, will contain unavailability data associated with Planned Outages of RTUs.

(5)	If the QSE or TO cannot resolve the telemetry data issue within two Business Days, it shall provide an estimated time of resolution.  Each QSE and TO shall notify ERCOT as soon as practicable when the telemetry data issue is resolved.

[NOGRR177: Replace Section 7.3.3 above with the following upon system implementation of NPRR857:] - 7.3.3 Data from WAN Participants to ERCOT (1) Each WAN Participant shall provide telemetered measurements over the ERCOT WAN on modeled Transmission Elements as required by the Protocols and the ERCOT Nodal ICCP Communication Handbook. (2) WAN Participants shall provide Real-Time monitoring of power system quantities to ERCOT as defined in the Protocols and the ERCOT Nodal ICCP Communication Handbook. ERCOT shall work with WAN Participants to determine the required data using the methodology presented in the Protocols. Transmission Element status and analog measurements that the Transmission Operators (TOs) and QSEs define in the Network Operations Model shall, at a minimum, be provided to ERCOT. Ultimately, it is the responsibility of the TOs and QSEs to provide all data requested by ERCOT. (3) Real-Time telemetry data from QSEs used to supply power or Ancillary Services shall be integrated by ERCOT and checked against settlement meter values on a monthly basis. (4) Each QSE and TO shall notify ERCOT as soon as practicable when there are known telemetry data issues (telemetry data will not be available or is unreliable for operational purposes). Each QSE or TO shall address the known telemetry data issue with either a correction of the telemetry data as soon as practicable, or a manual data replacement, if available, as soon as practicable. The report, as outlined in Section 9.2.2, Real-Time Data Monitor, will contain unavailability data associated with Planned Outages of RTUs. (5) If the QSE or TO cannot resolve the telemetry data issue within two Business Days, it shall provide an estimated time of resolution. Each QSE and TO shall notify ERCOT as soon as practicable when the telemetry data issue is resolved.

#### 7.3.3.1		Weather Zone Data

(1)	A TSP that is responsible for providing Weather Zone tie-line measurement data to ERCOT is required to establish a backup to the primary source.

(2)	TSPs having an Energy Management System (EMS) with a native ICCP application capable of four second periodic data set transfers with minimum 300 points per data set, and hot standby backup ICCP servers with automatic fail-over capability, shall provide an additional ICCP association across the ERCOT WAN for the transfer of Weather Zone tie line measurements.  ICCP nodes should exist at primary and backup facilities.

- 7.3.4	Resolving Real-Time Data Issues that affect ERCOT Network Security Analysis

(1)	Real-Time telemetry data issues that affect ERCOT’s Network Security Analysis (NSA) are issues that cause invalid State Estimator solutions.

(2)	Manually replaced telemetry data is data entered by a QSE or TO on their systems that is transmitted to ERCOT via ICCP in place of the normal points experiencing an issue.

(3)	ERCOT shall notify the QSE or TO responsible for the telemetry data when a Real-Time telemetry data issue affects ERCOT’s NSA.  ERCOT shall request each QSE or TO  address the Real-Time telemetry data issue with either manually replaced telemetry data if secondary sources are available or correction of the telemetry data issue as soon as practicable.  If the QSE or TO cannot address the issue within 10 minutes of notification, the QSE or TO shall coordinate with ERCOT to verbally agree to the best assumed data value(s).  The QSE or TO shall use verbally agreed data to manually replace the data point to reflect the best assumed data value(s).  The QSE or TO and ERCOT shall review the manually replaced telemetry data; the QSE or TO shall update the manually replaced telemetry data to reflect the best assumed data value(s) until the Real-Time data issue is resolved.

(4)	If the QSE or TO cannot resolve the Real-Time telemetry data issue that is affecting ERCOT’s NSA within two Business Days, it shall provide an estimated time of resolution.  Each QSE or TO shall notify ERCOT when the Real-Time telemetry data issue that was affecting ERCOT’s NSA is resolved.

### 7.3.5	TSP and QSE Telemetry Restoration

(1)	Real-Time telemetry data shall be restored using criteria and procedures pursuant to Protocol Section 3.10.7.5, Telemetry Requirements.

[NOGRR177: Replace Section 7.3.5 above with the following upon system implementation of NPRR857:] ### 7.3.5 TO and QSE Telemetry Restoration (1) Real-Time telemetry data shall be restored using criteria and procedures pursuant to Protocol Section 3.10.7.5, Telemetry Requirements.

### 7.3.6	General Telemetry Performance Criterion

(1)	All Real-Time telemetry as required by the Protocols shall meet the State Estimator requirements pursuant to Protocol Section 3.10.9, State Estimator Requirements, and the telemetry requirements pursuant to Protocol Section 3.10.7.5, Telemetry Requirements.

## 7.4	Calibration and Testing of Telemetry Responsibilities

(1)	It is the responsibility of the owner of telemetry equipment to ensure that calibration, testing and other routine maintenance of equipment is performed consistently with the provisions of the Protocols and Good Utility Practice.

## 7.5	Competitive Renewable Energy Zone Circuits and Stations

(1)	For each new Competitive Renewable Energy Zone transmission line, listed below, an associated communications path should be established to provide a high degree of dependability, security, and immunity from interference.  Additionally this communications path should support high bandwidth (155 mb/s or greater), low latency (unidirectional delay no greater that one millisecond per 100 miles), and be engineered to meet 99.999% availability with capacity reserved for regulated utility protection, monitoring and control.  Redundant communication paths are required unless this necessitates retrofitting existing facilities.   Competitive Renewable Energy Zone consists of the following 345 kV circuits and associated stations:

(a)	Bluff Creek to Brown double circuit;

(b)	Brown to Killeen double circuit;

(c)	Clear Crossing to Willow Creek double circuit;

(d)	Killeen to Salado add second circuit;

(e)	Scurry County South Switching Station to West Shackelford double circuit;

(f)	Scurry County South Switching Station to Tonkawas double circuit;

(g)	Scurry County South Switching Station to Long Draw Station double circuit;

(h)	Dermott Switching Station to Scurry County South Switching Station double circuit;

(i)	Dermott Switching Station to Willow Creek double circuit;

(j)	Central Bluff to Bluff Creek double circuit;

(k)	West Shackelford to Navarro/Sam Switch double circuit;

(l)	Sand Bluff Station to Divide double circuit capable;

(m)	Bearkat Station to Sand Bluff station double circuit capable;

(n)	Riley to Tesla double circuit;

(o)	Tesla to Edith Clarke double circuit;

(p)	North McCamey to Odessa double circuit capable;

(q)	Bakersfield to North McCamey double circuit capable;

(r)	Bakersfield to Big Hill double circuit capable;

(s)	Big Hill to Kendall double circuit capable;

(t)	Big Hill to Twin Butte double circuit capable;

(u)	Riley to Edith Clarke double circuit;

(v)	Ogallala to Windmill double circuit capable;

(w)	Ogallala to Tule Canyon double circuit capable;

(x)	Windmill to Alibates double circuit capable;

(y)	Tule Canyon to Cottonwood Station double circuit;

(z)	Tule Canyon to Cross to Tesla double circuit;

(aa)	Cottonwood Station to Dermott Switching Station double circuit;

(bb)	Cottonwood Station to Edith Clarke double circuit;

(cc)	Alibates to Tule Canyon double circuit;

(dd)	Gray to Tesla double circuit;

(ee)	Gray to Alibates double circuit;

(ff)	Edith Clarke to Clear Crossing double circuit;

(gg)	Sweetwater East to Central Bluff double circuit;

(hh)	Tonkawa to Sweetwater East double circuit;

(ii)	Long Draw Station to Sand Bluff Station double circuit capable;

(jj)	Long Draw Station to Grelton Station double circuit capable;

(kk)	Grelton Station to Odessa double circuit capable;

(ll)	Riley to Bowman double circuit;

(mm)	Riley to West Krum double circuit;

(nn)	West Krum to Anna double circuit;

(oo)	Willow Creek to Hicks double circuit;

(pp)	Bowman to Jacksboro double circuit capable;

(qq)	Jacksboro to Willow Creek double circuit;

(rr)	Willow Creek to Parker double circuit; and

(ss)	Clear Crossing to West Shackelford double circuit.