## Slide 1
Large Flexible Load Issues
Summary of ERCOT suggestions for Manual Loadshed and UFLS

## Slide 2: Manual Loadshed goal changes to accommodate Large Flexible Loads
Simple Implementation
Implement Loadshed in similar fashion that operators have been trained on.
Ensure LFL are shed to aid in avoiding Emergencies
Allow optional treatment for these loads but then based on this selection having clear rules
Address complications for TO’s due to different participations of LFL in Market
Minimize the need for system changes

## Slide 3: Concept
Require connecting Large Loads to register as either Firm/Native Load or LFL
Apply Loadshed rules based on registration type
  Firm/Native loads continue to use existing table
  LFL would require creation of a new Loadshed process/table
    LFL loadshed percentages would be calculated based on registered capacity of load.
Instructions for manual Loadshed:
  LFL would be to the QSE
  Firm/Native Load would be to TO
Instructions for LFL Loadshed would occur before Firm/Native loadshed instructions to TOs
  Firm Load Shed would be minimized by using this sequence

## Slide 4: Example of two Manual Loadshed tables
ERCOT Firm Load Shed Table | 
Transmission Operator | 2021 Total Transmission Operator Load (% MW)
AEP Texas Central Company | 8.41
Brazos Electric Power Cooperative Inc. | 4.85
Brownsville Public Utilities Board | 0.37
Bryan Texas Utilities | 0.52
CenterPoint Energy Houston Electric LLC | 25.89
City of Austin DBA Austin Energy | 3.54
City of College Station | 0.28
City of Garland | 0.73
City of Lubbock | 0.58
CPS Energy (San Antonio) | 6.44
Denton Municipal Electric | 0.48
GEUS (Greenville) | 0.14
Golden Spread Electric Cooperative Inc. | 0.36
Lamar County Electric Cooperative Inc* | 0.07
LCRA Transmission Services Corporation | 5.89
Oncor Electric Delivery Company LLC | 35.47
Rayburn Country Electric Cooperative Inc. DBA Rayburn Electric | 1.34
South Texas Electric Cooperative Inc. | 1.92
Texas-New Mexico Power Company | 2.72
ERCOT Total | 100.00
ERCOT LFL Load Shed Table | 
Qualified Scheduling Entity | 2021 Total QSE LFL Loadshed percentage(% MW)
QSE-1 | 8.41
QSE-2 | 4.85
QSE-3 | 0.37
QSE-4 | 0.52
QSE-5 | 25.89
QSE-6 | 3.54
QSE-7 | 0.28
QSE-8 | 0.73
QSE-9 | 0.58
QSE-10 | 6.44
QSE-11 | 0.48
QSE-12 | 0.14
QSE-13 | 0.36
QSE-14 | 0.07
QSE-15 | 5.89
QSE-16 | 35.47
QSE-17 | 1.34
QSE-18 | 1.92
QSE-19 | 2.72
ERCOT Total | 100.00

## Slide 5: LFL Manual Loadshed concept
Consider trigger level for LFL
  Shouldn’t shed LFL providing Ancillary Services prior to EEA
Should be at a level to ensure all LFL load is shed before Firm Loadshed
Trigger level should be aligned in the range where LFL would economically desire to be off anyway

## Slide 6: UFLS Loadshed goals to accommodate Large Flexible Loads
Simple Implementation
Implement Loadshed in similar fashion that operators have been trained on.
Ensure LFL are shed Automatically in steps aligned with Firm load UFLS.
Allow optional treatment for these loads but then based on this selection having clear rules.
Address complications for TO’s due to LFL being more responsive to market

## Slide 7: Concept
Require connecting Large Loads to register as either Firm/Native Load or LFL
Based on this selection apply UFLS rules
LFL loads would be required to install and maintain UFLS based on same settings as Firm/Native Load UFLS.
LFL loads would certify their UFLs and provide details to TSP and ERCOT when established or modified.

## Slide 8: UFLS example on an LFL site
5800
6895
5000
5500
6000
6800
H
LD
-
1
LD
-
2
LD
-
3
LD
-
4
LD
-
5
LD-6
-
5%
UFLS
10%
UFLS
10%
UFLS
Total
25%
UFLS