## Slide 1: LFL-47: Consider Voltage Control/Voltage Stability
Problem Statement:
  Large Flexible Loads vary their consumption frequently and enough to impact nearby voltage.
Considerations:
  How much variation in load is expected?
  Frequent variations could be difficult to manage SOLs
    Manually switched Capacitor & Reactors are not sufficient
    Dynamic Reactive Devices are better suited, when no Generation nearby
    Time delay to allow for switching actions?
  Transmission or Distribution connected?
    Power Factor obligations identified in Interconnection Agreement, .97pf

## Slide 2: LFL-47: Consider Voltage Control/Voltage Stability
  Modeling
    How is variability captured in studies, LDF’s?
  How do TSPs manage voltage with current large variable loads?
    Steel Mills
  Should LFL follow a Voltage Setpoint?
    Similar to a Generation Resource
    Possible?
  Should Large load have a Voltage Ride Through Requirement?
    Simultaneous trip could result in large loss of load event
    High Frequency Event
    Are TSAT models needed to simulate large load loss contingency or impacts on GTCs.

## Slide 3: LFL-33: Rules related to RAS/CMPs
Considerations:
  Constraint Management Plans (CMPs)
    Used where SCED is unable to resolve Transmission violation. See CMP definition
    RAPs – Cannot include Generation dispatch or Load shed
    Mitigation Plans – Post Contingency action, used when no dispatch solution is available. Load shed
    PCAP – Pre Contingency action, line switching that would isolate load post contingency. Reliability tool.
    AMP – Limited to series device insertion
  Remedial Action Schemes
    NOGRR215
    More discussion with TSPs needed