## Slide 1
ECRS Deployment Procedure – Preliminary Thoughts
June 17, 2022
WMWG
ERCOT Balancing Operations Planning Staff

## Slide 2: Background on ECRS
ERCOT Contingency Reserve Service (ECRS) is a service that is provided using capacity that can be sustained at a specified level for two consecutive hours and is used to restore or maintain the frequency of the ERCOT System:
  In response to significant depletion of RRS;
  As backup Regulation Service;
  By providing energy to avoid getting into or during an Energy Emergency Alert (EEA); and
  Upon detection of insufficient capacity for net load ramps during periodic checking of available capacity.
This presentation will share ERCOT’s preliminary thoughts on deployment procedure for ECRS.

## Slide 3: ECRS Deployment/Release Introduction
There are four situations that will cause ECRS to be deployed:
  Disturbance conditions such as a unit trip, sustained frequency decay or sustained low frequency operations;
  Detection of insufficient capacity for net load ramps during periodic checking of available capacity;
  SCED not having enough energy available; or
  When Resource(s) providing ECRS are the only reasonable option(s) available to the Operator for resolving local issues.
In each of these cases, the ERCOT operator will make the final decision and initiate the deployment.
The ERCOT operator shall deploy ECRS in amounts sufficient to respond to the operational circumstances. This means that ECRS may be deployed partially over time or may be deployed in its entirety.
  To the extent that ERCOT deploys a Non-Controllable Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire Ancillary Service Resource Responsibility or, if only partial deployment is possible, skip the Load Resource with the block deployment option and proceed to deploy the next available Resource.

## Slide 4: ECRS Deployment/Release Conditions
ERCOT will deploy ECRS when frequency drops below 59.91 Hz and available Reg-Up is not sufficient to restore frequency.
ERCOT may deploy ECRS under the following conditions,
  When (Physical Responsive Capability (PRC) – 3200 – (10-minute net load ramp) < X MW, deploy sufficient ECRS capacity so that (HASL – Gen – IRR Curtailment) – (30-minute net load ramp) > Y MW.*
  When (Physical Responsive Capability (PRC) – 3200 – (10-minute net load ramp) < Z MW, deploy all ECRS capacity.*
  Non-Controllable Load Resources that are providing ECRS will be separated into deployment groups as defined in Nodal Protocol Section 6.5.9.4.2 EEA Levels paragraph (2). Non-Controllable Load Resources that are providing ECRS can be deployed during an Emergency Condition either individually, in groups, or as an entire block providing Non-Spin. Deployments that do not encompass an entire block may be done to manage inertia, congestion, or for other local needs.
If a condition other than those listed above indicates that additional capacity may be needed to manage reliability, operators will evaluate the system condition and deploy ECRS as needed if no other better options are available to resolve the system condition. Under emergency, the emergency process will govern the deployment of ECRS.
*This is a preliminary metric that ERCOT is considering to use to identify when ECRS on SCED Dispatchable resources may be deployed.

## Slide 5: ECRS Deployment & Recall Steps – SCED Dispatchable Resources
SCED dispatchable Generation Resources (including Quick Start Generation Resources) & Controllable Load Resources that are providing ECRS (Automatic and Manual Deployment)
  Upon receiving an ECRS deployment instruction via ICCP, the QSE shall adjust the telemetered ECRS Ancillary Service Schedule for the SCED dispatchable Resources.
  ERCOT will automatically calculate new HASL constraints for SCED using the telemetry of the Resource’s ECRS Ancillary Service Schedule.
  The QSE must, at a minimum, ensure that the Emergency Ramp Rate represented by the Resource’s ramp rate curve is sufficient to allow SCED to fully Dispatch the Resource’s ECRS Resource Responsibility within 10 minutes.
  QSEs can restore ECRS Ancillary Service Schedule once the ICCP Deployment signal reflects zero MW ECRS deployment.

## Slide 6: ECRS Deployment & Recall Steps – Generation Resources operating in Synchronous Condenser mode
Generation Resources operating in synchronous condenser fast response mode using Resource Status ONECRS
  ERCOT will deploy and recall Generation Resources operating in synchronous condenser fast response mode carrying ECRS (ONECRS) using ICCP Deployment instruction that is separate from other ECRS Deployment instruction for other SCED dispatchable resources providing ECRS.
  ONECRS resources may be deployed automatically when frequency falls below 59.80 Hz or manually (A) to meet NERC Standard defined in Nodal Protocol Section 6.5.7.6.2.4 (2) OR (B) during scarcity conditions following declaration of an EEA Nodal Protocol Section 6.5.7.6.2.4 (5).
  Automatic Deployment and Recall
    Automatic deployment based on Frequency threshold of 59.80 Hz
    Full response must be provided in 20 seconds
    When Frequency hits 59.80 Hz, ERCOT will follow-up with the ONECRS ICCP Deployment Instructions that equals the current ECRS Ancillary Service Responsibility of Resources telemetering Resource Status of ONECRS.
      ERCOT expects automatic response and QSE should only use the ONECRS ICCP Deployment instructions for maintaining Resources output to match the ONECRS ICCP Deployment instruction.
    Following the recovery of system frequency (currently 59.98 Hz), and ERCOT not under an EEA, ERCOT will reset the ONECRS ICCP Deployment signal to reflect a zero MW ECRS deployment.
    QSEs can restore ONECRS capability and stop generating MW from ONECRS Resources once the ONECRS ICCP Deployment signal reflects zero MW ECRS deployment.

## Slide 7: ECRS Deployment & Recall Steps – Generation Resources operating in Synchronous Condenser mode
Manual Deployment and Recall under EEA Condition
  Generally, manual deployment of Resources telemetering Resource Status of ONECRS will happen following declaration of an EEA Level 1 but before ERCOT enters into EEA level 2.
    When ERCOT declares EEA Level 2 or EEA Level 3 without declaring EEA level 1, ERCOT may immediately deploy ONSC Resources.
  Manual deployment instructions equal to ECRS Ancillary Service Responsibility will be sent through ICCP to deploy all available ECRS MW capacity from Generation Resources providing ECRS that have a Resource Status of ONECRS.
  QSEs will have 10 minutes following the receipt of ERCOT deployment instructions to provide energy deployments from Generation Resources providing ECRS that have a Resource Status of ONECRS.
  Following the recovery of PRC above 2500 MW and stable system frequency, ERCOT will reset the ONECRS ICCP Deployment signal to reflect zero MW deployment. QSEs can then restore ONECRS capability and stop generating MW from ONECRS Resources.
Manual Deployment and Recall under non-EEA Condition
  Manual deployment instructions totaling QSEs ECRS Ancillary Service Responsibility will be sent through ICCP to deploy all available ECRS MW capacity from Generation Resources providing ECRS that have a Resource Status of ONECRS.
  QSEs will have 10 minutes following the receipt of ERCOT deployment instructions to provide energy deployments from Generation Resources providing ECRS that have a Resource Status of ONECRS.
  Following the recovery of system frequency (currently 59.98 Hz), and ERCOT not under an EEA, ERCOT will reset the ECRS ICCP Deployment signal to reflect zero MW deployment. QSEs can then restore ONECRS capability and stop generating MW from ONECRS Resources.

## Slide 8: ECRS Deployment & Recall Steps – Non-Controllable Load Resources
Load Resource that is not a Controllable Load Resource with ECRS Ancillary Service Resource Responsibility
  Non-Controllable Load Resources that are providing ECRS will be separated into deployment groups as defined in Nodal Protocol Section 6.5.9.4.2 EEA Levels paragraph (2).
  The QSE will be sent a Resource-specific Dispatch Instruction for the ECRS deployment indicating a time and date stamp, QSE, Dispatch Asset Code, and Deployed MW.
  The Dispatch Instruction must include the expected amount of capacity that will be expected to be dropped by the Load Resource within 10 minutes.
  The QSE will ensure that the ECRS Ancillary Service Schedule telemetry for that Load Resource has been reduced to zero within one minute of receiving the Dispatch Instruction.
  The Load Resource must, at a minimum, be capable of remaining deployed until recalled.
  ERCOT shall recall ECRS deployment provided from Non-Controllable Load Resources once PRC is above a pre-defined threshold (above 2500 MW and stable system frequency).
  A QSE with a Non-Controllable Load Resource that has provided ECRS will ensure that the Load energy and ECRS capability is restored within three hours of the recall instruction of the ECRS deployment issued by ERCOT. If the QSE cannot restore within three hours of the ERCOT recall instruction of the ECRS deployment, the ECRS obligation must be replaced by the QSE from other ECRS qualified Resources capable of providing the service.
    The QSE will ensure that the ECRS Ancillary Service Schedule telemetry for a Non-Controllable Load Resource continuously and accurately represents the amount of Load Resource that has been restored following a recall instruction and is available for subsequent deployment.

## Slide 9: Next Steps
ERCOT will continue to work on refining this preliminary procedure over the next couple weeks.
ERCOT plans to bring the procedure ERCOT expects to use when ECRS is implemented in a document format with any refinements following today’s discussion to July WMWG.