## Slide 1
Resource Integration Topics
Jay Teixeira
ERCOT
Resource Integration Working Group
June 28, 2022

## Slide 2: Quarterly Stability Assessment (QSA)
Planning Guide 5.9
Next Deadline for QSA
If a GINR is not included in QSA, its Initial Synchronization date will be automatically delayed to the next quarter
All-Inclusive Generation Resource Initial Synchronization Date | Last Day for an IE to meet prerequisites as listed in paragraph (4) below | Completion of Quarterly Stability Assessment
Upcoming January, February, March | Prior August 1 | End of October
Upcoming April, May, June | Prior November 1 | End of January
Upcoming July, August, September | Prior February 1 | End of April
Upcoming October, November, December | Prior May 1 | End of July

## Slide 3: Quarterly Stability Assessment (QSA)
Planning Guide 5.9, Quarterly Stability Assessment
Issue’s seen in previous QSA’s
  10 day comment period for FIS
    Needs to be complete before QSA deadline
    TSPs need to plan for it
  Dynamic/PSCAD Model Review
    Dependent on FIS Stability study
    Need to meet PG 6.9 15 to 30 days prior to QSA deadline
PSSE Model Quality Test Required
PSCAD Model Quality Test and Unit Model Validation required
TSAT Model Required – If PSSE model is UDM, then TSAT model should be UDM

## Slide 7: RI Handbook Update
Resource Interconnection Handbook Updated
  Version 1.92, dated 6/15/2022
  Market Notice Sent 6/21/2022

## Slide 8: Use of current Commissioning Checklist
ERCOT New Generator Commissioning Checklist
  Posted 2/21/2022
  New submittals must use this version
  https://www.ercot.com/files/docs/2022/02/22/ERCOT%20New%20Generator%20Commissioning%20Checklist.docx

## Slide 9: BTM Load Requirements
The RE has provided ERCOT and the Interconnected TSP the technical equipment and load data to be used in modeling studies for the new netting loads being added.
Required system studies including new netting loads have been completed and approved by TSP and ERCOT. This includes any modifications to existing FIS studies or new studies that impact the system.
One of the following has been completed:
  Amendments to the SGIA indicating new netting loads have been signed by all three parties (TDSP, RE, Load Entity). The SGIA should reflect the servable load. OR
  Amendments to the SGIA indicating new netting loads has been signed by the TSP and RE and the TSP has submitted a written notification agreeing to proceed with the energization of the new load per the amended SGIA. OR
  Written notification from the TSP agreeing to proceed with the energization of the new load per the approved studies.
Reactive study with the addition of the new netting loads has been approved by ERCOT. For existing Resource not currently in the Interconnection process as a repower, the Reactive study can be submitted in RIOO-RS.
EPS Meter Proposal including the new netting loads has been approved by ERCOT.
Updated Resource Registration data that includes the addition of the PUN loads and any other topology changes at the Station. In addition, the Production Load Date that the Network Operations Model has been updated, including required telemetry. The current timeline to model the new netting load is a 90-day PLD. For additional information regarding the modeling schedule, please refer to the Production Load Schedule. Furthermore, the following prerequisites must be met prior to RARF approval to add the new PUN Load:
  Required system studies have been completed and approved.
  Meet one of the following requirements stated in item #3.
  Reactive study with the addition of the new netting load has been completed and approved.
  EPS meter proposal has been submitted and approved by ERCOT metering.
  Any request for Interim updates requires approval from ERCOT Modeling.
Checklist Part 1 to Energize the new netting loads and associated equipment has been submitted in RIOO-IS for Generation in the interconnection process or RIOO-RS for other generation.

## Slide 10: Load Compliance Checklist
Requirements for New Netting Loads Added to New or Existing Generation sites.
  Must be completed and submitted along with Part 1 Energization Checklist ERCOT New Generator Commissioning Checklist.
RE is responsible for re-evaluating the Reactive study to assess the impact of the additional PUN load to ensure the Resource’s ability to meet VSS requirements is not impacted.
    Example: 100MW Resource, VSS requirement is +/- 32.9 MVAr. Addition of 50MW PUN load consuming 4 MVAr’s being connected to the MV bus. The Reactive study should demonstrate that the Resource is able to meet +/- 32.9MVAr with the additional 50MW load.

## Slide 11: FIS Study for Co-located load
Resource Entities adding large behind-the-meter loads to their facilities must coordinate with their interconnecting TSP and ERCOT on appropriate interconnection studies:
  Studies should follow all applicable guidelines: NERC FAC-002, NERC TPL 001-5, ERCOT Planning Guide Section 4.
  Study must include scenario with the Load online and Generation offline.
Studies:
  Steady-state required
  Short circuit required or provide suitable justification
  Stability study- Most large loads will require a stability study. TSP will inform the load customer if no stability study is needed after careful consideration by TSP and ERCOT
  SSR if needed

## Slide 12: Telemetry location for ESR MVAr
ESR MVAr telemetry during charging scenarios should be represented on the Unit.
  ESR Load MVAr should always be 0.
  Same sign convention as Unit MVAr.
Load MVAr = 0
Load MW=Charging
Unit Gross MW = 0
Unit Gross MVAr
Telemetry during Charging-Leading

## Slide 13: Active RR’s
None

## Slide 14: Other contact information
ResourceIntegrationDepartment@ercot.com is distribution list for Resource Integration department
Mailing List
  RESOURCE_INTEGRATION@LISTS.ERCOT.COM

## Slide 15: Questions?
Thank you!