## Slide 1
ERCOT Frequency Control Report
June 2022
ERCOT
Operations Planning
PDCWG | July 20th, 2022

## Slide 2: Summary of May 2022
CPS1: 172.96%
Current CPS1 12-Month Rolling Average: 172.67%
0 BAAL Exceedance(s)
2 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2022 RMS1 Statistics
  Mean: 15.43 mHz
  Min: 12.43 mHz
  Max: 19.12 mHz
Energy Statistics
  Total Energy: 42,088,672 MWh
  Wind Energy: 9,677,677 MWh
  Percent Energy from Wind: 22.99 %
  Solar Energy: 2,672,960 MWh
  Percent Energy from Solar: 6.35%
Minimum System Inertia
  Mean: 250,219 MW*s
  Max: 296,135 MW*s on June 28th
  Min: 206,265 MW*s on June 15th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
June-22 CPS1 (%): 172.96
Notes: 1. 61.90%@ 6/20/2022 HE 20:00
Expected Generation Deviation
Between 19:00-20:00 the Expected gen dev remained negative. The largest expected gen dev was -2914MW @ 19:30 PM with signification contribution from solar and wind generation.
IRR Ramps
Between 19:00-20:00 solar ramped down by ~3400 MW
Between 19:00-20:00 wind ramped down by ~1400 MW
Regulation: Regulation up was exhausted during the later half of the hour. SCED was run multiple times and Multiple SCED offsets were applied and the largest being 500 MW at 7:30 PM
2. 97.97% @ 6/26/2022 HE 16:00
Expected Generation Deviation
Expected generation deviation remained negative during later part of the hour. The largest expected gen dev was -28642MW @ 3:49PM with significant contribution from solar generation.
IRR Ramps
Between 3:35pm to 3:50 pm solar ramped down by ~1000 MW.
Regulation: Regulation up was exhausted during the solar ramp duration. SCED was run multiple times and SCED offset of 300 MW was applied @3:47PM.

## Slide 5: BAAL Exceedances & Violations
There are 0 BAAL exceedance(s) in June.

## Slide 6: 15-Minute Average CPS1%
June-22 CPS1 (%): 172.96
Notes: Overall the 15 min CPS1 score is above 160, Between 19:00 and 20:00 ,the CPS1 is between 110 to 150 due to solar down ramps.
19:45 to 20:00 110 due to solar down ramps

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 172.67%
Notes: 12 month rolling average CPS1 score is 172.67, which is good and CPS1 score for June is slightly higher than the last month.

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year is so far slightly smaller overall compared with the 2021.
  Mean: 15.43 mHz
  Min: 12.43 mHz
  Max: 19.12 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by month
15.56Mhz on avg for June 2022

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Same data but only showing for the last 10 years

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison
Notes: Comparison of frequency profile for June 2021 and June 2022, Overall frequency profiles is are comparable to each other.

## Slide 13: Frequency Profile Comparison
Notes: Comparison of frequency profile for June 2020 and June 2022, very similar trend here. we see fewer instances of frequency hovering at or below the lower deadband in June 2022.

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error
Notes: We did not make time error corrections. Time error started to go down around the 20th due to a significant solar and wind ramp coincided with each other. Also temperature picks up in late June.

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 42,088,672 MWh
There is an increase in total energy compared to last year

## Slide 22: Total Energy from Wind Generation
Notes: 9,677,677 MWh
We see notable decrease in the wind energy production in June.

## Slide 23: % Energy from Wind Generation
Notes: 22.99%
of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 2,672,960 MWh
There is also a notable increase in solar energy production in May.

## Slide 25: % Energy from Solar Generation
Notes: 6.35% of total energy was provided by soalr generation

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia =206,265 MW*s on 06/15/2022
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 250,219 MW*s
Max: 296,135 MW*s on June 28th
Min: 206,265 MW*s on June 15th

## Slide 28: Questions?
Thank you!