## Slide 1
Regulation Bias Analysis Post SCR-773
June 2022
ERCOT
Operations Planning
PDCWG | July 20th, 2022

## Slide 2
Discussion Points
Current GTBD Parameters & References
Metric to measure Regulation bias and performance
Regulation Deployed comparison for last three months.
Total Regulation (net) Deployed Comparison
Regulation Deployed 15-minute interval comparison by each hour for 2020, 2021, and 2022 months
Regulation Exhaustion Rate
Regulation bias for consecutive 5-min SCED intervals
Time Error & Contributing Factors
Summary

## Slide 3: Current GTBD Parameters
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 – K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 – 10:05 AM – K6 Changed from 0 to 0.5
2/12/19 – 2:15 PM – K6 changed from 0.5 to 1.0
3/12/19 – 2:10 PM – PWRR Threshold from 10 to 15 MW/min
3/19/19 – 2:15 PM – PWRR Threshold from 15 to 20 MW/min
4/01/19 – 10:00 AM – K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 – 1:15 PM – Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – 1:10 PM – K5 changed from 0.4 to 0.5, Max Integral ACE feedback changed from 160 to 200, PWRR Threshold changed from 25 to 30
6/17/20 – 10 AM - PWRR Calculation method changed from Direct to Interpolated
9/1/20 – 11 AM - Max Integral ACE Feedback changed from 200 to 250
9/3/20 – 3 PM - Max Integral ACE Feedback changed from 250 to 300
9/4/20 – 3 PM - Max Integral ACE Feedback changed from 300 to 250
6/1/21 – 10:00 AM – K8 Changed from 0 to 0.5, PSRR Threshold changed to 10
6/2/21 – 10:00 AM – PSRR Threshold changed from 10 to 20
6/3/21 – 10:00 AM – K8 Changed from 0.5 to 0.75
6/4/21 – 10:00 AM – K8 Changed from 0.75 to 1
9/2/21 – 10:00 AM – PSRR Threshold changed to 30
6/7/22 – 10:30 AM – K7 Changed from 0 to 0.5, PDCTRR Min/Max Threshold changed to 10 MW/min
6/8/22 – 10:30 AM – PDCTRR Min/Max Threshold changed from 10 to 20
6/9/22 – 10:30 AM – K7 Changed from 0.5 to 0.75
6/10/22 – 10:30 AM – K7 Changed from 0.07 to 1.0
**** - PDCTRR Min/Max Threshold changed to 20 MW/min

## Slide 4: Projected Wind Ramp Rate MAE
Notes: For intra-hour wind ramp forecast, SCED PWRR MAE is fairly consistent and smaller than the persistence forecast across the board.

## Slide 5: Projected Wind Ramp Rate Error
Notes: PWRR error is higher during the ramp up and ramp down hours. Regardless of the ramping magnitude, SCED PWRR is consistent and performing significantly better than the persistence forecast

## Slide 6: Projected Solar Ramp Rate MAE
Notes: For intra-hour solar ramp forecast, SCED PSRR is performing significantly better especially during the solar up ramp and down ramp hours compared to the persistence forecast

## Slide 7: Projected Solar Ramp Rate Error
Notes: Similar to wind, generally we see bigger forecast errors during ramping periods.

## Slide 8: References

## Slide 9
Metrics to Measure SCR-773 Performance
Trend and monitor the regulation deployed by hour.
Set target of 50 MW for total regulation deployed by hour for peak hours.
Set target of 85% for the number of intervals where regulation deployment was both up and down for peak hours.
Track the Regulation exhaustion rate for all hours (not to exceed 5%).
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours.

## Slide 10: Total Regulation Deployed Comparison
Total regulation deployed for the last three months.

## Slide 11: Total Regulation Deployed Comparison - Monthly
Notes: Total regulation deployed comparison in the last 3 months: Overall the trends have been very similar. A bit more reg up deployment during in the middle of the day due to higher than expected load.

## Slide 12: Metric 1: Regulation Deployed Comparisons
Trend and monitor the regulation deployed by hour.

## Slide 13: Regulation Deployed Comparison

## Slide 14: Regulation Deployed Comparison
Notes: Overall Regulation up deployment in June is consistent with that of previous two years.

## Slide 15: Regulation Deployed Comparison
Notes: Overall Regulation down deployment in June is consistent with that of previous two years.

## Slide 16: Metric 2: Total Regulation Deployed Comparisons
Set target of 50MW for total regulation deployed by hour for peak hours.

## Slide 17: Total Regulation Deployed Comparison
Notes: Total regulation deployed compared with pervious two year. More reg up deployed during sunst and more reg down deployed due to sun rise.

## Slide 18: Metric 3: 15-min Intervals Where Both REGUP/REGDN Were Deployed
Set target of 85% for the number of intervals where regulation deployment was both up and down.

## Slide 19: “Zero” Crossing Regulation
Notes: For zero crossing regulation usage, the smaller zero-crossing reg percentages occurred during sun rise and sun set hours.

## Slide 20: “Zero” Crossing Regulation
Notes: Overall, we see that it is over 77% for all hours, which shows a good balance of deploying both Reg up and down.

## Slide 21: Metric 4: Regulation Exhaustion Rate
Track the regulation exhaustion rate for all hours (not to exceed 5%.)

## Slide 22: Regulation Exhaustion Rate
Notes: Average regulation up exhaustion rate for all hours is 1.46 %

## Slide 23: Regulation Exhaustion Rate
Notes: Average regulation down exhaustion rate for all hours is 6.37 %

## Slide 24: Metric 5: Stats on REGUP Bias for Consecutive 5-min Intervals
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5-minute intervals for peak hours.

## Slide 25: Regulation Bias for Consecutive SCED Intervals
Notes: Regulation up bias occurrence for consecutive SCED intervals for all hour is 97 and peak hours is 41.

## Slide 26: Regulation Bias for Consecutive SCED Intervals
Notes: Regulation down bias occurrence for consecutive SCED intervals for all hour is 143 and peak hours is 7.

## Slide 27: Time Error and Contributing Factors
Accumulated Time Error, Load and Wind Ramp, PWRR Error, Start-Up/Shut-Down Hours, STLF Error, and Expected Generation Deviation.

## Slide 28: Time Error Accumulation
Notes: Hourly time error accumulation is fairly similar compared with last years.

## Slide 29: Load Profile
Notes: There is a big increase in total load in June due to high temperatures.

## Slide 30: Net Load Profile
Notes: The netload peak in June is also higher than that of last two years

## Slide 31: Load Ramp
Notes: Hourly load ramp is higher in the middle of the day compared to last two years’.

## Slide 32: Wind Profile
Notes: Hourly wind generation is much higher compared to the last two years’.

## Slide 33: Start-Up & Shut-Down Hours
Notes: Net capacity on start up and shut down is fairly consistent with last two years.

## Slide 34: Short-Term Load Forecast Error
Notes: Forecast – Actual
+ve Error => Over forecasted load
-ve Error +> Under forecasted load
The STLF errors is kept quite small for most of the hours.

## Slide 35: STLF Error Chart
Notes: Error = Forecast – Actual
Min,Max, 10th, 90th percentile
15 minute intervals
Max Positive Forecast Error:
6/4/2022 13:00 -> 397.80 MW
Max Negative Forecast Error:
6/13/2022 21:15-> -230.24 MW

## Slide 36: Expected Generation Deviation

## Slide 37: Expected Generation Deviation
Notes: Breakdown by resource type and we see significant contribution from wind and solar during the ramping hours

## Slide 38: Expected Generation Deviation
Notes: Comparing renewables vs non-renewables. Again, IRR resources are the main contributor for most part of the day.

## Slide 39: Questions?
Thank you!