## Slide 1
Analysis on Changing Generation Cost Scaling in HRUC
Dave Maggio
ERCOT
Technical Advisory Committee (TAC)
July 27, 2022

## Slide 2: Background
The cost scaling factor for Reliability Unit Commitment (RUC) was introduced with Nodal Protocol Revision Request (NPRR) 864 in October 2018.
  The scaling factor modifies the Start Up and Minimum Energy Costs for Resources with a cold start time of one hour or less.
The intent was to make short lead time Resources appear more economical in the RUC optimization.
  Under the previous operational approach, this would allow ERCOT to defer commitment decisions and provide market participants additional time to self-commit their Resources.
  Ideally, it was hoped that commitments would not be needed due the deferred commitments.

## Slide 3: Background
The cost scaling of short lead time Resources is no longer effective with ERCOT’s current operational approach.
  The scaling has led to ERCOT Operators needing to make many of their RUC decisions outside of the economic-based, RUC recommendations. This can lead to inefficiencies in the commitment decisions.
  Changing the cost scaling factors to 100% will help ensure the commitment decisions better reflect the economically optimal commitment decision.
This will benefit both ERCOT and the general market.
  Commitment of the most economic set of Resources.
  Potential decreases in make whole payments.
  Less burden on ERCOT staff to perform extra studies outside of the RUC tool.

## Slide 4: Changes to Scaling
Original
Scaling Removed

## Slide 5: Summary of Study Cases
September 2nd, 2021 7:00
  No commitments were RUC recommended
  Resources committed for hours ending 13-21
  Maximum aggregate High Sustained Limit (HSL) of committed Resources was 1,141 MW
  High Ancillary Service Limit (HASL) margins were between -1,798 MW and 424 MW
October 3rd, 2021 6:00 (available in appendix)
  Most commitments were RUC recommended
  Resources committed for hours ending 13-23
  Maximum aggregate HSL of committed Resources was 889 MW
  HASL margins were between -5,223 MW and -51 MW
February 23rd, 2022 4:00 (available in appendix)
  No commitments by operators were RUC recommended
  Resources committed for hours ending 8-14
  Maximum aggregate HSL of committed Resources was 1,176 MW
  HASL margins were between -531 MW and 1100 MW for HE8-14
April 22nd, 2022 5:00 (available in appendix)
  Commitments by Operators were all recommended by RUC
  WESTEX constraint was the reason given by operators
  Resources were committed for hours ending 11-17
  Maximum aggregate HSL of committed Resources was 531 MW

## Slide 6: September 2nd, 2021 7:00 Case

## Slide 7: Comparison of HSLs and Low Sustained Limits (LSLs) for Recommended Commitments
Chart: Sum of HSL for Committed Resources
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Original | 0 | 0 | 346 | 951 | 1841.8 | 1649 | 1694 | 443 | 1169 | 1305 | 558 | 152 | 0 | 0
Scaling Removed | 0 | 0 | 395 | 952 | 1896.4 | 1662 | 1717.4 | 1015 | 1128 | 1283 | 540.5 | 0 | 0 | 0
Chart: Sum of LSL for Committed Resources
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Original | 0 | 0 | 92 | 389 | 1011.9 | 868 | 868 | 189 | 405 | 501 | 132 | 80 | 0 | 0
Scaling Removed | 0 | 0 | 36 | 169 | 591.5 | 514 | 568.4 | 179 | 187 | 252 | 39 | 0 | 0 | 0
Note: HSL for each Resource was maximum value over commitment block
LSL for each Resource was minimum value over commitment block

## Slide 8: Comparison of Recommended Commitments by Lead Time
Chart: MWhs Recommended by Lead Time
| Extension | Short Lead Time | Medium Lead Time | Long Lead Time | Very Long Lead Time
Original | 0 | 10108.8 | 0 | 0 | 0
Scaling Removed | 919 | 2677.3 | 2075 | 4918 | 0
Chart: Number of Resource Hours Recommended by Lead Time
| Extension | Short Lead Time | Medium Lead Time | Long Lead Time | Very Long Lead Time
Original | 0 | 176 | 0 | 0 | 0
Scaling Removed | 2 | 51 | 13 | 17 | 0
Note
Extensions: Resource Output is Extended
Short Lead Time: 0 < Startup Time < 1 hour
Medium Lead Time: 1 <= Startup Time < 5 hours
Long Lead Time: 5 <= Startup Time < 10 hours
Very Long Lead Time: 10 hours <= Startup Time

## Slide 9: Comparison of Recommended Commitments by Lead Time
Chart: Original Case
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Extension | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Short Lead Time | 0 | 0 | 346 | 951 | 1841.8 | 1649 | 1694 | 443 | 1169 | 1305 | 558 | 152 | 0 | 0
Medium Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Very Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chart: Scaling Removed
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Extension | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435 | 484 | 0 | 0 | 0
Short Lead Time | 0 | 0 | 0 | 203 | 755.4 | 521 | 576.4 | 113 | 226 | 226 | 56.5 | 0 | 0 | 0
Medium Lead Time | 0 | 0 | 395 | 280 | 280 | 280 | 280 | 280 | 280 | 0 | 0 | 0 | 0 | 0
Long Lead Time | 0 | 0 | 0 | 469 | 861 | 861 | 861 | 622 | 622 | 622 | 0 | 0 | 0 | 0
Very Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note: HSL for each Resource was maximum value over commitment block
Note
Extensions: Resource Output is Extended
Short Lead Time: 0 < Startup Time < 1 hour
Medium Lead Time: 1 <= Startup Time < 5 hours
Long Lead Time: 5 <= Startup Time < 10 hours
Very Long Lead Time: 10 hours <= Startup Time

## Slide 10: Conclusions from the Analysis
Generally, changing the scaling induces the RUC optimization to recommend more extensions and medium to long lead time Resources, as opposed to leaning heavily on short lead time Resources.
  This conclusion may not hold for cases with very low projected HASL margins when the RUC optimization is already recommending commitment of all or most available Resources.
Cases with the scaling removed tend to have similar amounts of aggregate HSL capacity, but lower aggregate LSL amounts and fewer Resources
  The optimization typically chooses larger Resources when scaling is removed.
  There is less out-of-market impact when the aggregate LSL of RUC-committed Resources is lower.
“Scaling Removed” cases were more aligned with Operator actions but could better ensure committed Resources are the most economic choice.
  RUC optimization production cost reductions ranged from 13% to 60% across the four cases studied, with the scaling changed from 20% to 100%. *
  The commitment of Resources with lower costs will lead to a reduction in potential make-whole payments that must be collected
Compared the production cost amounts between the scaling removed case and the original case using the unscaled cost of the short lead time Resources

## Slide 11: Process for Updating the RUC Scaling Parameter
The scaling parameter for Off-Line Resources having a cold start time of one hour or less is driven by paragraph (9) of Protocol Section 5.5.2, Reliability Unit Commitment (RUC) Process.
Changing this parameter does not require an NPRR and it can be updated through a recommendation by the TAC and approval by the ERCOT Board.
  Table in Protocol 5.5.2(9):
ERCOT staff is asking for TAC to make that recommendation with approval by the ERCOT Board at their next meeting.

## Slide 12: Appendix of Additional Case Studies

## Slide 13: October 3rd, 2021 6:00 Case

## Slide 14: Comparison of HSLs and LSLs for Recommended Commitments
Note: HSL for each Resource was maximum value over commitment block
LSL for each Resource was minimum value over commitment block
Chart: Sum of HSL for Committed Resources
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Original | 0 | 0 | 226 | 1253 | 1740 | 2883 | 3809 | 4507 | 4206.4 | 4804.4 | 4644 | 2806.4 | 2068 | 246.9
Scaling Removed | 0 | 0 | 56.5 | 1237 | 1817 | 2887 | 3798.3 | 4507 | 4206.4 | 4804.4 | 4625.6 | 2814.5 | 2124 | 246.9
Chart: Sum of LSL for Committed Resources
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Original | 0 | 0 | 16 | 127 | 304 | 555 | 1158.2 | 1337.2 | 1113.2 | 1567.2 | 1435.2 | 713.2 | 474.5 | 133
Scaling Removed | 0 | 0 | 4 | 111 | 196 | 457 | 831 | 1337.2 | 1113.2 | 1567.2 | 1261 | 441 | 329 | 133

## Slide 15: Comparison of Recommended Commitments by Lead Time
Chart: MWhs Recommended by Lead Time
| Extension | Short Lead Time | Medium Lead Time | Long Lead Time | Very Long Lead Time
Original | 612.9 | 11415.2 | 19312 | 1380 | 0
Scaling Removed | 1146.9 | 7651.7 | 22242 | 1610 | 0
Chart: Number of Resource Hours Recommended by Lead Time
| Extension | Short Lead Time | Medium Lead Time | Long Lead Time | Very Long Lead Time
Original | 4 | 188 | 64 | 6 | 0
Scaling Removed | 7 | 126 | 76 | 7 | 0
Note
Extensions: Resource Output is Extended
Short Lead Time: 0 < Startup Time < 1 hour
Medium Lead Time: 1 <= Startup Time < 5 hours
Long Lead Time: 5 <= Startup Time < 10 hours
Very Long Lead Time: 10 hours <= Startup Time

## Slide 16: Comparison of Recommended Commitments by Lead Time
Note: HSL for each Resource was maximum value over commitment block
Chart: Original Case
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Extension | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 0 | 0 | 118 | 9.9
Short Lead Time | 0 | 0 | 226 | 254 | 616 | 727 | 1529 | 1578 | 1277.4 | 1390.4 | 1955 | 1148.4 | 714 | 0
Medium Lead Time | 0 | 0 | 0 | 999 | 1124 | 1926 | 2050 | 2699 | 2699 | 2699 | 2459 | 1658 | 999 | 0
Long Lead Time | 0 | 0 | 0 | 0 | 0 | 230 | 230 | 230 | 230 | 230 | 230 | 0 | 0 | 0
Very Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chart: Scaling Removed
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Extension | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 195 | 217 | 240 | 9.9
Short Lead Time | 0 | 0 | 56.5 | 113 | 113 | 308 | 869.3 | 1578 | 1277.4 | 1390.4 | 1501.6 | 331.5 | 113 | 0
Medium Lead Time | 0 | 0 | 0 | 1124 | 1704 | 2349 | 2699 | 2699 | 2699 | 2699 | 2699 | 2036 | 1534 | 0
Long Lead Time | 0 | 0 | 0 | 0 | 0 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 0 | 0
Very Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note
Extensions: Resource Output is Extended
Short Lead Time: 0 < Startup Time < 1 hour
Medium Lead Time: 1 <= Startup Time < 5 hours
Long Lead Time: 5 <= Startup Time < 10 hours
Very Long Lead Time: 10 hours <= Startup Time

## Slide 17: Feb 23rd, 2022 4:00 Case

## Slide 18: Comparison of HSLs and LSLs for Recommended Commitments
Note: HSL for each Resource was maximum value over commitment block
LSL for each Resource was minimum value over commitment block
Chart: Sum of HSL for Committed Resources
| 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Original | 0 | 0 | 511.5 | 664 | 618 | 714 | 226 | 226 | 674 | 942 | 748 | 748 | 2634.7 | 4100.7 | 4564.6 | 4564.6 | 3786.8 | 2871 | 2269
Scaling Removed | 126 | 126 | 239 | 676 | 454 | 805.3 | 454 | 454 | 854 | 976 | 976 | 976 | 2724 | 4767.8 | 5165 | 4409.8 | 4055.8 | 2886 | 2262
Chart: Sum of LSL for Committed Resources
| 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Original | 0 | 0 | 172 | 200 | 200 | 224 | 16 | 16 | 71 | 134 | 74 | 74 | 908.6 | 1193.6 | 1184 | 1184 | 968 | 809 | 707
Scaling Removed | 64.2 | 64.2 | 72.2 | 184.2 | 96 | 260 | 96 | 96 | 139 | 154 | 154 | 154 | 606 | 1081 | 1282.6 | 1026 | 1008.5 | 698 | 473

## Slide 19: Comparison of Recommended Commitments by Lead Time
Chart: MWhs Recommended by Lead Time
| Extension | Short Lead Time | Medium Lead Time | Long Lead Time | Very Long Lead Time
Original | 6590 | 14756.9 | 9516 | 0 | 0
Scaling Removed | 8487 | 8052.4 | 13822 | 2179.3 | 846
Chart: Number of Resource Hours Recommended by Lead Time
| Extension | Short Lead Time | Medium Lead Time | Long Lead Time | Very Long Lead Time
Original | 32 | 183 | 30 | 0 | 0
Scaling Removed | 43 | 96 | 43 | 15 | 9
Note
Extensions: Resource Output is Extended
Short Lead Time: 0 < Startup Time < 1 hour
Medium Lead Time: 1 <= Startup Time < 5 hours
Long Lead Time: 5 <= Startup Time < 10 hours
Very Long Lead Time: 10 hours <= Startup Time

## Slide 20: Comparison of Recommended Commitments by Lead Time
Note: HSL for each Resource was maximum value over commitment block
Chart: Original Case
| 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Extensions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 513 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 757 | 240
Short Lead Time | 0 | 0 | 511.5 | 664 | 618 | 714 | 226 | 226 | 161 | 307 | 113 | 113 | 1640.7 | 1498.7 | 1439.6 | 1439.6 | 1420.8 | 1755 | 1909
Medium Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 1967 | 2490 | 2490 | 1731 | 359 | 120
Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Very Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chart: Scaling Removed
| 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Extensions | 126 | 126 | 126 | 126 | 0 | 0 | 0 | 0 | 513 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 1282 | 1108
Short Lead Time | 0 | 0 | 113 | 322 | 226 | 322 | 226 | 226 | 113 | 113 | 113 | 113 | 674 | 1003.8 | 1401 | 1037.8 | 1206.8 | 616 | 226
Medium Lead Time | 0 | 0 | 0 | 228 | 228 | 228 | 228 | 228 | 228 | 228 | 228 | 228 | 741 | 2490 | 2490 | 2490 | 1967 | 741 | 851
Long Lead Time | 0 | 0 | 0 | 0 | 0 | 255.3 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 582 | 582 | 190 | 190 | 190 | 20
Very Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504 | 57 | 57 | 57 | 57 | 57 | 57
Note
Extensions: Resource Output is Extended
Short Lead Time: 0 < Startup Time < 1 hour
Medium Lead Time: 1 <= Startup Time < 5 hours
Long Lead Time: 5 <= Startup Time < 10 hours
Very Long Lead Time: 10 hours <= Startup Time

## Slide 21: Apr 22nd, 2022 5:00 Case

## Slide 22: Comparison of HSLs and LSLs for Recommended Commitments
Note: HSL for each Resource was maximum value over commitment block
LSL for each Resource was minimum value over commitment block
Chart: Sum of HSL for Committed Resources
| 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Original | 1350.2 | 749.4 | 558.4 | 502.4 | 2685 | 2695 | 2097 | 1259.6 | 1166.4 | 817.4 | 1205.6 | 921.2 | 168
Scaling Removed | 1350.2 | 805.9 | 511.9 | 455.9 | 2439.1 | 3117.1 | 2452.2 | 1636.6 | 1200.2 | 780.6 | 1123.6 | 752.7 | 570.6
Chart: Sum of LSL for Committed Resources
| 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Original | 853.4 | 383 | 303 | 250 | 1470.8 | 1498.8 | 1249.8 | 692.8 | 696.8 | 582.8 | 791.8 | 513 | 90
Scaling Removed | 853.4 | 387 | 272 | 219 | 1028 | 1421 | 1207 | 720.8 | 597.2 | 344 | 592.6 | 326 | 80

## Slide 23: Comparison of Recommended Commitments by Lead Time
Chart: MWhs Recommended by Lead Time
| Extension | Short Lead Time | Medium Lead Time | Long Lead Time | Very Long Lead Time
Original | 122 | 9522.6 | 4073 | 0 | 0
Scaling Removed | 523 | 6482.5 | 5892 | 1872 | 0
Chart: Number of Resource Hours Recommended by Lead Time
| Extension | Short Lead Time | Medium Lead Time | Long Lead Time | Very Long Lead Time
Original | 1 | 166 | 25 | 0 | 0
Scaling Removed | 1 | 106 | 28 | 8 | 0
Note
Extensions: Resource Output is Extended
Short Lead Time: 0 < Startup Time < 1 hour
Medium Lead Time: 1 <= Startup Time < 5 hours
Long Lead Time: 5 <= Startup Time < 10 hours
Very Long Lead Time: 10 hours <= Startup Time

## Slide 24: Comparison of Recommended Commitments by Lead Time
Note: HSL for each Resource was maximum value over commitment block
Chart: Original Case
| 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Extension | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0
Short Lead Time | 906.2 | 749.4 | 558.4 | 502.4 | 1049 | 1059 | 674 | 728.6 | 635.4 | 653.4 | 1041.6 | 760.2 | 168
Medium Lead Time | 0 | 0 | 0 | 0 | 934 | 934 | 776 | 531 | 531 | 164 | 164 | 39 | 0
Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Very Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chart: Scaling Removed
| 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
Extension | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523
Short Lead Time | 906.2 | 805.9 | 511.9 | 455.9 | 599.1 | 812.1 | 360.2 | 436.6 | 435.2 | 274.6 | 617.6 | 219.6 | 47.6
Medium Lead Time | 0 | 0 | 0 | 0 | 1124 | 1369 | 1211 | 966 | 531 | 272 | 272 | 147 | 0
Long Lead Time | 0 | 0 | 0 | 0 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 0
Very Long Lead Time | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note
Extensions: Resource Output is Extended
Short Lead Time: 0 < Startup Time < 1 hour
Medium Lead Time: 1 <= Startup Time < 5 hours
Long Lead Time: 5 <= Startup Time < 10 hours
Very Long Lead Time: 10 hours <= Startup Time