## Slide 1
Bearkat – North McCamey – Sand Lake 345-kV Transmission Addition Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
July 27, 2022

## Slide 2: Overview
  This is a Tier 1 project that is estimated at $477.6 Million
  Address the reliability need driven by rapid load growth in the Delaware Basin area
  Improve capability to import power into the Delaware Basin area
LCRA Transmission Services Corporation (LCRA TSC), Wind Energy Transmission Texas (WETT), and Oncor jointly submitted the Bearkat – North McCamey – Sand Lake 345-kV Transmission Line Addition Project for Regional Planning Group (RPG)

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review indicated reliability planning criteria violation
  Potential steady-state voltage instability under certain NERC Category P7 contingency (i.e., N-1 condition)
System improvement is needed to meet reliability planning criteria

## Slide 5: Comparison of Project Options
In the Delaware Basin Load Integration Study, ERCOT evaluated a number of options and developed a road map to improve the capability to import power into the Delaware Basin area
    Stage 1: Adding a second circuit on the existing Big Hill – Bakersfield 345-kV line, endorsed in June 2021 and is expected to be implemented in 2023
    Stage 2: Adding a new Bearkat - North McCamey - Sand Lake double-circuit 345-kV line (~$371 Million in 2019 dollar and $477.6 million in 2021 dollar, estimated new rights-of-way: 164 miles)
    Stage 5: Adding a new Faraday - Lamesa - Clearfork - Riverton double-circuit 345-kV line (Stage 5 upgrade, estimated cost: $444 Million in 2019 dollar, estimated new rights-of-way: 193 miles)
The Stage 1 upgrade was endorsed in 2021
The Stage 2 upgrade is selected as preferred option over the Stage 5 upgrade due to relatively less new rights-of-way and lower project cost

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for the Stage 2 upgrade and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  the Stage 2 upgrade did not cause new or additional congestion
  no potential future generation were found which may impact reliability issue
  the load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation:
Based on the review, ERCOT will recommend the Board endorse the Stage 2 upgrade to address the reliability need in the Delaware Basin area
TSPs expect to implement the upgrades by June 2026
Estimated Capital Cost: $477.6 Million
ERCOT will recommend that the ERCOT Board designate the Stage 2 upgrade as critical to the reliability of the ERCOT System pursuant to PUCT Substantive Rule 25.101(b)(3)(D)

## Slide 9: ERCOT Recommendation: Stage 2 Upgrade
Build a new double-circuit 345-kV line from existing Bearkat Substation to existing North McCamey Substation (~71 miles), with normal and emergency ratings of at least 2,564 MVA
Build a new double-circuit 345-kV line from existing North McCamey Substation to existing Sand Lake Substation (~94 miles), with normal and emergency ratings of at least 2,564 MVA
Reconfigure each of the existing substations into a breaker-and-a-half substation (as a minimum configuration)

## Slide 10: Map of Stage 1, 2 and 5 Upgrades