## Slide 1
ERCOT Analysis of Environmental Protection Agency (EPA) Federal Implementation Plan (FIP) Regional Ozone Transport Rule
Woody Rickerson
Vice President of System Planning and Weatherization
Technical Advisory Committee Meeting
July 27, 2022
ERCOT Public

## Slide 2: Cross-State Air Pollution Rule (CSAPR) Federal Implementation Plan (FIP)
The EPA proposes that emission reductions for 26 states, including Texas, are necessary to address upwind states’ interstate transport obligations. Under the proposed rule, the FIP would establish nitrogen oxides (NOx) emissions budgets beginning in ozone season (May 1- September 30) 2023 for Electric Generating Units sources. ERCOT has performed a preliminary analysis of the potential effect the adoption of this rule would have on the ERCOT grid in 2026. The analysis assumed the retirement of 10,803 MW (installed capacity) of thermal generation, which included 8,203 MW of coal-fired generation at 7 locations, and 2,600 MW of gas-fired generation at 4 locations.
The analysis included the addition of future generation (20,035 MW, only 4% representing thermal generation) that currently meets ERCOT Planning Guide Section 6.9 requirements but did not consider any generation that might be built as a direct result of the loss of the 10,803 MW leaving the market.
In this preliminary analysis, ERCOT looked at four areas of concern for maintaining reliability.

## Slide 3: Cross-State Air Pollution Rule (CSAPR) Federal Implementation Plan (FIP)
The results of the preliminary analysis in 2026 include:
Steady-State Transmission Analysis showed significant impacts to the reliability of the transmission system resulting in $1.2 to $1.5 billion to resolve the local reliability issues. The study did not include ERCOT wide regional analysis, however based on the recent studies, there could be an accelerated need for an additional $2.7 to $5.2 billion of transmission improvements to improve the ERCOT regional transfer capability after the retirement of the CSAPR-affected generation.
If the CSAPR-affected generation is retired, the probability of load shed for summer 2026 increases by almost nine times at 8pm when solar generation becomes unavailable.
The ERCOT Outage Approval process will only be able to approve approximately 1/3 of the expected maintenance outages required by the remaining thermal units in 2026 after the removal of the CSAPR-affected generation.
The loss of the CSAPR-affected generation will reduce the gross inertia capacity of the system by 13%. This will likely result in increased out of market instruction by ERCOT to maintain minimum amounts of inertia needed to maintain reliability.

## Slide 4: Generation Removed from Service in 2026 for ERCOT Analysis
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | INSTALLED CAPACITY RATING (MW) | SUMMER CAPACITY (MW)
COLETO CREEK | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 650.0 | 655.0
FAYETTE POWER U1 | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 615.0 | 604.0
FAYETTE POWER U2 | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 615.0 | 599.0
FAYETTE POWER U3 | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 460.0 | 437.0
J K SPRUCE U1 | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 555.0 | 560.0
LIMESTONE U1 | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 893.0 | 824.0
LIMESTONE U2 | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 956.8 | 836.0
MARTIN LAKE U1 | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 893.0 | 800.0
MARTIN LAKE U2 | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 893.0 | 805.0
MARTIN LAKE U3 | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 893.0 | 805.0
SAN MIGUEL U1 | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 430.0 | 391.0
TWIN OAKS U1 | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 174.6 | 155.0
TWIN OAKS U2 | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 174.6 | 155.0
GRAHAM STG 2 | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 387.0 | 390.0
GREENS BAYOU CTG 73 | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 72.0 | 56.0
GREENS BAYOU CTG 74 | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 72.0 | 56.0
GREENS BAYOU CTG 81 | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 72.0 | 56.0
GREENS BAYOU CTG 82 | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 72.0 | 50.0
GREENS BAYOU CTG 83 | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 72.0 | 56.0
GREENS BAYOU CTG 84 | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 72.0 | 56.0
T H WHARTON POWER CTG 51 | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 85.0 | 56.0
T H WHARTON POWER CTG 52 | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 85.0 | 56.0
T H WHARTON POWER CTG 53 | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 85.0 | 56.0
T H WHARTON POWER CTG 54 | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 85.0 | 56.0
T H WHARTON POWER CTG 55 | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 85.0 | 56.0
T H WHARTON POWER CTG 56 | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 85.0 | 56.0
W A PARISH CTG 1 | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 16.3 | 13.0
W A PARISH STG 1 | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.9 | 169.0
W A PARISH STG 2 | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.9 | 169.0
W A PARISH STG 3 | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 299.2 | 240.0
W A PARISH STG 4 | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 580.5 | 527.0
 |  |  |  |  | Totals | 10,803.7 | 9,800.0

## Slide 5: Generation Removed from Service in 2026 for ERCOT Analysis

## Slide 6: West Virginia v. EPA Decision
U.S. Supreme Court issued opinion on 6/30/22 striking down Clean Power Plan rule as exceeding EPA’s authority under Clean Air Act (CAA)
In that rule, EPA had set CO2 emissions limits for coal and gas plants based on reductions that would be expected if operators were to shift to renewable technologies, asserting that this “generation-shifting” was the “best system of emissions reductions” (BSER) available.
In reviewing rule, Supreme Court invoked “major questions doctrine”: agency decisions involving “economic and political significance” require agency to show “clear congressional authorization.”
Held: section 111(d) of CAA did not clearly authorize EPA to set emissions limits based on generation-shifting as a BSER. BSERs must be source-specific emissions-reduction technologies, not industry-wide methods of limiting emissions.
Use of major questions doctrine likely raises the bar for EPA and all other federal agencies in regulating important economic and political matters.
Court’s rejection of generation-shifting was based on specific language of CAA provision. Whether generation-shifting under other EPA rules may be allowed depends on the language of the statutory provision relied on in each case.
If an EPA rule has a significant economic impact, and EPA cannot point to clear congressional authorization, that rule may be susceptible to being overturned.