## Slide 1
Roanoke Area Upgrades Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
July 27, 2022

## Slide 2: Overview
  This is a Tier 1 project that is estimated at $ 285.9 Million
  Address the reliability need driven by rapid load growth in Roanoke area
  Provide operational flexibility in Roanoke area
Oncor submitted the Roanoke Area Upgrade Project for Regional Planning Group review

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review indicated reliability planning criteria violation
System improvement is needed to meet reliability planning criteria
 | Thermal Overloads and Low Voltages
Total | 7.5 miles of 138-kV lines 25.9 miles of 345-kV lines (4) 345/138-kV transformer (5) 138-kV buses with low voltages

## Slide 5: Comparison of Project Options
ERCOT analyzed four options and short-listed three options
Among the short-listed three options, Option 2 provides better operational flexibility and better long-term load serving capability for future load growth in the aera
Option 2 is the preferred option
 | Option 2 | Option 3 | Option 4
Met ERCOT and NERC Reliability Criteria? | Yes | Yes | Yes
Long-term Load Serving Performance | Better | Yes | Yes
Improved Operational Flexibility | Better | Yes | Yes
Capital Cost Estimates* | $286 M | $264 M | $254 M

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 2 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 2 did not cause new or additional congestion
  no potential future generation were found which may impact reliability issue
  the load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation:
Based on the review, ERCOT will recommend the Board endorse Option 2 to address the reliability need in the Roanoke area
TSP expect to implement the upgrades by May 2025
Estimated Capital Cost: $286 Million
ERCOT will recommend that the ERCOT Board designate Option 2 as critical to the reliability of the ERCOT System pursuant to PUCT Substantive Rule 25.101(b)(3)(D)

## Slide 9: ERCOT Recommendation: Option 2
Construct a new Ramhorn Hill 345-kV switching station in a 10-breaker breaker-and-a-half arrangement tapped into existing double-circuit Hicks to Willow Creek 345-kV lines
Construct a new Dunham 345-kV switching station in a 10-breaker breaker-and-a-half arrangement tapped into existing Lewisville to Krum West and Lewisville to Roanoke 345-kV lines
Construct two new Ramhorn Hill to Dunham 345-kV transmission lines, with conductor rated to at least 2987 MVA, in a new (estimated 18.4-mile) right-of-way installed on new triple-circuit towers leaving one 138-kV vacant position
Rebuild Exchange to Roanoke 345-kV double-circuit lines, upgrading both with conductors rated to at least 2987 MVA, using separate double-circuit capable structures for each line. The line rating will be 1912/1912 MVA limited by terminal equipment at Roanoke
Construct a new Exchange to Roanoke 138-kV circuit, with conductor rated to at least 764 MVA, using one of the Exchange to Roanoke 345-kV line double-circuit capable structures
Construct a new Exchange 345/138-kV Switching Station, adjacent to Alliance 345-kV substation, with two new 600 MVA (nameplate) transformers in an 8-breaker 345-kV breaker-and-a-half bus arrangement and a 9-breaker 138-kV breaker-and-a-half arrangement. The normal/emergency ratings of the new transformers will be 700/750 MVA
Convert the existing Alliance 345-kV load serving substation to 138-kV load serving operation
Construct a new Exchange to Alliance 138-kV double-circuit line with conductors rated to at least 746 MVA
Construct a new Alliance to Keller Magnolia and Alliance to Heritage 138-kV double-circuit line with conductors rated to at least 746 MVA in a new (estimated 1.4-mile) right-of-way
Upgrade the existing Keller Magnolia to Heritage 138-kV line with conductor rated to at least 746 MVA to be installed on Alliance to Keller Magnolia and Alliance to Heritage 138-kV double-circuit towers
Upgrade the existing Heritage to Keller Magnolia Tap double-circuit lines with conductors rated to at least 746 MVA
Construct a new 138-kV switching station at Keller Wall Price in a 6-breaker ring bus arrangement
Disconnect the double-circuit Heritage to Keller Magnolia Tap lines at Keller Magnolia Tap and terminate both at Keller Wall Price by constructing two new 0.3-mile 138-kV transmission lines added to the existing Keller Magnolia Tap to Keller Wall Price right-of-way with both new line conductors rated to at least 746 MVA
Retire Keller Magnolia Tap

## Slide 10: Option 2