## Slide 1
August 18, 2022 | PDCWG
August 19, 2022 | WMWG
Preliminary Methodology to Determine 2023 ECRS Requirements
ERCOT Staff

## Slide 2: Introduction
ERCOT is in the process of implementing ERCOT Contingency Reserve Service (ECRS).
  ERCOT is targeting to implement ECRS prior to the “EMS freeze” period (around May 2023 – Jan 2024)
This presentation will discuss a proposed* methodology to determine the minimum quantities for ECRS in 2023. A spreadsheet that contains ECRS quantities from August 2022 through July 2023 that have been computed using this proposed methodology have been posted to today’s meeting page.
  ERCOT is seeking stakeholder feedback on the proposed ECRS methodology.
Note on Non-Spinning Reserve Service (Non-Spin) quantities post ECRS implementation
ECRS and Non-Spin differ in the reliability risks these services address, qualification criteria, response time and duration. As a result, upon ECRS’ implementation, Non-Spin requirement cannot entirely be substituted by the amount of ECRS procured as was originally proposed during NPRR863 discussions.
That said, ERCOT expects the risks that Non-Spin is used to cover will evolve upon ECRS’ implementation. Hence the methodology to determine Non-Spin quantities in a world where ECRS exists may need revisions.
  ERCOT plans to discuss the Non-Spin methodology that will apply with ECRS’ implementation as a part of the annual AS Methodology review process.
  * Note, ERCOT may refine the ECRS methodology further as a part of the annual effort to review the methodology for determining Ancillary Service (AS) quantities (AS Methodology).
Notes: WMWG | June 2022 ECRS Deployment Procedure (Part 1) | https://www.ercot.com/files/docs/2022/06/17/Preliminary_ECRS_Deployment_Procedure_v0_JuneWMWG.pptx
WMWG | July 2022 ECRS Deployment Procedure (Part 2) | https://www.ercot.com/files/docs/2022/07/26/Preliminary_ECRS_Deployment_Procedure_v0_JulyWMWG.pptx

## Slide 3: ECRS Requirements Methodology
ECRS is a service that is provided using capacity that can be sustained at a specified level for two consecutive hours and is used to restore or maintain the frequency of the ERCOT System:
  In response to significant depletion of RRS;
  As backup Regulation Service;
  By providing energy to avoid getting into or during an Energy Emergency Alert (EEA); and
  Upon detection of insufficient capacity for net load ramps.
ERCOT is proposing to compute ECRS requirements as the sum of,
  capacity needed to recover frequency following a large unit trip and
  capacity needed to support sustained net load ramps.
The next few slides will discuss the detail about each of these components that establish the ECRS requirements.

## Slide 4: Method for Determining MWs needed for Frequency Recovery
Capacity needed to recover frequency from B-point (i.e., settling frequency) to 59.98 Hz is determined by using dynamic simulations/studies that are run at varying inertia levels.
In every simulation, a single medium-size unit is tripped offline such that the C-point (frequency nadir) is stays just above 59.7 Hz*.
Capacity needed to recover frequency using this approach is determined for each hour of each month using two years historical data.
*59.7Hz is the trigger frequency for Load Resources that are providing RRS using an under-frequency relay.
  MWneed = (59.98 Hz – FreqB-point) * (1% load in MW/0.1 Hz)
B-point (settling frequency) is determined using dynamic simulations/studies that are run at varying inertia levels. In every simulation, a single medium-size unit is tripped offline such that the C-point (frequency nadir) is stays just above 59.7 Hz*.
60 Hz
59.7 Hz
B-point
59.98 Hz

## Slide 5: MWs needed for Frequency Recovery
 | Min | Mean | Max
MWneed | 574 MW | 951 MW | 1,572 MW

## Slide 6: Method for Determining Additional MWs needed for sustained Net Load Ramps
Capacity needed to support sustained net load ramps will be computed using
  85th to 95th percentile of 30-minute ahead intra-hour net load forecast errors for same hour same month of previous two years
    The percentile associated with every hour will be determined based on the risk of net load up ramp. Periods where the risk of net load ramp is highest will use 95th percentile and 85th percentile for periods with lowest risks.
  An additional adjustment will be included to account for the impact of increase in over-forecast error from expected growth in solar generation installed capacity.

## Slide 7: Regulation usage and SCED offset Trends
As the solar installed capacity has increased, during the evening hours, the magnitude of 10-min solar ramps have increased and there has been more reliance on regulation up deployments and SCED offsets.

## Slide 8: Projected Solar Generation Installed Capacity

## Slide 9: Adjustment for Increase in Solar Installed Capacity
Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in 30-min ahead solar over forecast error per 1000 MW increase in installed solar capacity.
Additional ECRS per 1,000 MW increase in solar installed capacity
Adjustment for 2023 (Min: 0 MW | Mean: 68 MW | Max 283 MW)

## Slide 10: MWs needed for Intra-hour Net Load Forecast Errors
 | Min | Mean | Max
MWneed | 403 MW | 913 MW | 1,889 MW
Without Solar Adjustment
With Solar Adjustment
 | Min | Mean | Max
MWneed | 403 MW | 981 MW | 2,027 MW

## Slide 11: ECRS Requirement for 2023
Total ECRS requirement for every hour is computed as the sum of
  capacity needed to recover frequency following a large unit trip and
  capacity needed to support sustained net load ramps (with solar adjustment)
 | Min | Mean | Max
ECRS | 1,093 MW | 1,933 MW | 3,039 MW

## Slide 12: Summary and Next Steps
Using the preliminary* methodology to determine the minimum quantities for ECRS, hourly ECRS requirements in 2023 may vary between 1,093 and 3,039 MW.
  A spreadsheet that contains the associated ECRS quantities for January through July of 2023 have been posted to today’s meeting page.
ERCOT is seeking stakeholder feedback on the proposed ECRS methodology.
Lastly, ERCOT expects the risks that Non-Spin is used to cover will evolve upon ECRS’ implementation. Hence the methodology to determine Non-Spin quantities in a world where ECRS exists may need revisions.
  ERCOT plans to discuss the Non-Spin methodology that will apply with ECRS’ implementation as a part of the annual AS Methodology review process.
* Note, ERCOT may refine the ECRS methodology further as a part of the annual effort to review the AS Methodology).

## Slide 13
Appendix

## Slide 14: 30-min-ahead Intra-hour Netload Forecast Error

## Slide 15: 30-min-ahead Intra-hour Load Forecast Error

## Slide 16: 30-min-ahead Intra-hour Wind Forecast Error

## Slide 17: 30-min-ahead Intra-hour Solar Forecast Error

## Slide 18: Comparison between ECRS and Non-Spin
ECRS and Non-Spin differ in the reliability risks to be addressed, the response time and the duration requirement. It is not recommended to substitute Non-Spin requirement either entirely or partially by the amount of ECRS procured.
 | ECRS | Non-Spin
Reliability Objective | ECRS may be deployed to Help restore the frequency to 60 Hz within ten minutes of a significant frequency deviation Provide energy upon detection of insufficient capacity for net load ramps Provide energy to avoid or during the implementation of an EEA Provide backup to Reg-Up | Non-Spin may be deployed to provide additional capacity, During situations when there isn’t sufficient capacity for energy dispatch For intra-day forced outage of units and during sustained frequency decay or sustained low frequency operations. When SCED does not have enough energy available to execute successfully
Primary Forecast Risk | Errors in 5-minute load/wind/solar forecast that is used in SCED dispatch (via GTBD) | Errors in hourly load/wind/solar forecast that is used in RUC
Qualification Criteria | Provided using capacity that can be sustained at a specified level for two consecutive hours | Provided using capacity that can be sustained at a specified level for four consecutive hours
Response | Deployed within 10 minutes upon the receipt of deployment instruction | Deployed within 30 minutes upon the receipt of deployment instruction