## Slide 1: Ancillary Service (AS) Framework including ECRS to be implemented around mid 2023
*Quantities will be updated in this slide following kickoff of 2023 Ancillary Service Methodology effort.
For Discussion Purposes Only. The intent of this slide is to represent Ancillary Service (AS) Framework after ECRS is implemented around mid 2023. Protocol language prevails to the extent of any inconsistency with this one-page summary.
FFR
Triggered at 59.85 Hz and full response in 15 cycles
Once deployed, sustain for up to 15 mins. Once recalled, restore within 15 mins
Maximum 450 MW of RRS may be provided by FFR Resources
PFR
PFR capable capacity reserved on generators or Controllable Load Resources (CLR)
Minimum 1,150 MW must be provided by resources capable of PFR
Capacity that is used to provide RRS-PFR must be capable of being sustained for 1 hour
Load Resources with under frequency relay (UFR)
Triggered at 59.70 Hz and full response in 30 cycles
Sustain until recalled. Once recalled, restore within 3 hours
Beyond the minimum PFR, up to 60% of total RRS can come from Load Resources on UFR or FFR
Generation
Online or offline capacity that can be converted to energy within 10 minutes
Dispatched by SCED
Capacity that is used to provide ECRS must be capable of being sustained for 2 hours.
Load Resources (UFR not required)
Up to 50% of ECRS capacity can come from Load Resources with or without UFR
Once deployed, must respond within 10 minutes. Sustain until recalled. Restoration within 3 hours
Load Resources on Under Frequency Relay (UFR)
Primary Frequency Response (PFR)
Fast Frequency Response (FFR)
ERCOT Contingency Reserve Service (ECRS)
Load Resources may or may not be on UFR
10-minute ramp
Generators or Controllable Load Resources (CLRs) respond within 5 seconds to ERCOT LFC instructions
FRRS providers respond within 60 cycles of either its receipt of ERCOT instruction or at 59.91 Hz; 65 MW maximum for FRRS-Up, 35 MW maximum for FRRS-Down
Capacity that is used to provide conventional Regulation must be capable of being sustained for 1 hour
Regulation
X MW to X MW*
X to X MW*
X MW to X MW*
Responsive Reserve Service (RRS)
Online or offline capacity from generators and Load Resources that can be deployed within 30 minutes
Online capacity (EOC floor $75/MWh) dispatched by SCED; Offline capacity dispatched by XML instruction
Minimum 1,430 MW must be provided by SCED dispatchable Resources
Non-Controllable Load Resources may provide Non-Spin; UFR if available, must be disarmed in Real Time
Capacity that is used to provide Non-Spin must be capable of being sustained for 4 hours
Non-Spinning Reserve Service
X MW to X MW*
Overall A/S: X,XXX to X,XXX MW*
Last Edited on 08/03/2022