| NOGRR Number | 226 | NOGRR Title | Revision to 5% Transmission Operator (TO) Load Shedding Relay Set Point |
| --- | --- | --- | --- |
| Date |  | August 17, 2022 |  |

| Submitter’s Information |  |
| --- | --- |
| Name | Collin Martin; Andy Nguyen |
| E-mail Address | Collin.Martin@oncor.com; Andy.Nguyen@LCRA.org |
| Company | Oncor Electric Delivery Company LLC; Lower Colorado River Authority |
| Phone Number | 817-215-6174; 512-705-8618 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU); Cooperative |

Comments

In its February 16, 2022 comments, Oncor proposed that a more gradual frequency correction tool be implemented in lieu of changing the Stage 1 Under-Frequency Load Shed (UFLS) set point from 59.3 Hz to 59.4 Hz as originally proposed in Nodal Operating Guide Revision Request (NOGRR) 226, Revision to 5% Transmission Operator (TO) Load Shedding Relay Set Point.  This UFLS “kicker/anti-stall” proposal was intended to address a seeming mismatch between the existing UFLS set points and generator under-frequency protection, and to avoid some of the broader considerations associated with a complete change of the Stage 1 UFLS set point.  The UFLS “kicker/anti-stall” measures would reduce the likelihood of a UFLS operation contributing to generator instability during weak system conditions and address the dead-band issue between 59.3 Hz and 59.4 Hz in the event of a slow frequency decline similar to what occurred during Uri.  This automatic response would ensure that Load shed actions are implemented in a timely manner even if system operators are unable to manually shed load in time to arrest a frequency decline.

In March 2022, ERCOT offered to study the proposed “kicker/anti-stall” proposal and the associated frequency trigger points, percent of load to be shed at each point, and time delays, which were placeholder values in Oncor’s comments.  The results of this study were presented by ERCOT during the June 23, 2022 Operations Working Group (OWG) meeting.  ERCOT’s evaluation suggested that a 59.5 Hz frequency trigger is appropriate for the Supplemental Kicker/Anti-Stall UFLS Stages.  After subsequent discussions of these findings between ERCOT and the Joint Transmission Operator (TO) Commenters, the “kicker/anti-stall” measures are proposed in three stages instead of four, with 1.5% incremental Load relief at each stage, with a 30 second delay to trip between Stages 2 and 3.

These comments adjust these three parameters in the proposed Table 2, Supplemental Kicker/Anti-Stall UFLS Stages, in paragraph (1) of Section 2.6.1, Automatic Firm Load Shedding.  The Joint TO Commenters believe the values proposed in these comments strike the best balance between reliable system performance and TO/Transmission and/or Distribution Service Provider (TDSP) implementation logistics.  The Joint TO Commenters also recommend these NOGRR226 comments, if approved, become effective no sooner than 18 months following Public Utility Commission of Texas (PUCT) approval.

These comments are submitted on top of the February 16, 2022 Oncor comments.

| Revised Cover Page Language |  |
| --- | --- |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) adds provisions for Transmission Operator (TO) “kicker” or “anti-stall” automatic firm Load shedding at 59.5 Hz in order to improve reliability by mitigating the risk of a total system-wide Blackout. |
| Business Case | On February 15, 2021 the system-wide frequency fell below 59.4 Hz for approximately four minutes and twenty-four seconds but did not fall below 59.3 Hz which would have triggered TO Load shedding and increased the system frequency above 59.4 Hz. Generators are required to operate their generation reliably and without tripping for frequencies above 59.4 Hz. When the frequency falls below 59.4 Hz, there is risk of damage to turbine blades. In order to avoid this damage, a relay is triggered that will trip the generator Off-Line after nine minutes. To mitigate this issue, this NOGRR proposes that TOs make automatic Load reductions in small steps when frequency degrades to 59.5 Hz, with the goal of avoiding further frequency declines. LCRA recommends that the Dynamics Working Group (DWG) review the 58.9 Hz and 58.5 Hz TO Load shedding relay set points and determine if any changes are needed to these set points. |

Market Rules Notes

Please note the baseline language in the following section has been updated to reflect the incorporation of the following NOGRR(s) into the Nodal Operating Guide:

- NOGRR212, Related to NPRR1016, Clarify Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs) (unboxed 1/1/22)

  - Section 2.6.1

- NOGRR233, Related to NPRR1094, Allow Under Frequency Relay Load to be Manually Shed During EEA3 (incorporated 12/17/21)

  - Section 2.6.1

Proposed Guide Language Revision

2.6.1	Automatic Firm Load Shedding

(1)	At least 25% of the ERCOT System Load shall be equipped at all times with provisions for automatic Under-Frequency Load Shedding (UFLS) as described in this paragraph.  In the event of an under-frequency event, each Transmission Operator (TO) shall provide Load relief by shedding the required percentage of its Distribution Service Provider (DSP)-connected Load and transmission-level Customer Load using automatic under-frequency relays, as specified in the tables below.  For the purposes of this paragraph, the TO Load will be the amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, when the ERCOT frequency drops to the 59.5 Hz threshold.  As such, the amount of the TO Load relief will not include any Load that has already been shed prior to the 59.5 Hz frequency threshold.  The under-frequency relays shall be set to provide Load relief as follows:

Table 1: Standard UFLS Stages

| Frequency Threshold | TO Load Relief | Delay to Trip |
| --- | --- | --- |
| 59.3 Hz | At least 5% of the TO Load | No more than 30 cycles |
| 58.9 Hz | A total of at least 15% of the TO Load | No more than 30 cycles |
| 58.5 Hz | A total of at least 25% of the TO Load | No more than 30 cycles |

Table 2: Supplemental Kicker/Anti-Stall UFLS Stages

| Frequency Threshold | TO Load Relief | Delay to Trip |
| --- | --- | --- |
| 59.5 Hz | At least 1.5% of the TO Load | 90 seconds |
| 59.5 Hz | A total of at least 3.0% of the TO Load | 120 seconds |
| 59.5 Hz | A total of at least 4.5% of the TO Load | 150 seconds |

(2)	ERCOT will, prior to the peak each year, survey each TO’s compliance with the automatic Load shedding requirements described in paragraph (1) above, and report its findings to the Technical Advisory Committee (TAC).  For purposes of determining a TO’s compliance with this annual survey requirement, TO Load will be the total amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, at the specified time of the survey.  The TO shall identify those circuits armed with under-frequency relays, the corresponding amount of Load, and identify the frequency threshold.  A TO shall not equip the entirety of its Load shed obligation in any one tier, and should endeavor to shed in controlled amounts that equal the difference between the TO Load relief required for each tier.  If ERCOT identifies potential reliability issues related to distribution of Load shed across the tiers, ERCOT may require the TO to redistribute Load relief closer to the minimum amount required after submitting ERCOT’s proposal to redistribute Load relief to the TO and considering any comments submitted by the TO regarding the proposal.  Compliance with this annual survey does not excuse the TO from compliance with the requirements of paragraph (1) above in an actual frequency event.  To assist TOs, ERCOT will provide the TO’s inventory, including substation and capacity amounts, of registered Load Resources in its area within ten Business Days of receiving a request in writing from a TO.

(3)	Load utilized to meet the requirements of the Supplemental Kicker/Anti-Stall UFLS Stages may overlap with the load utilized to meet the 58.9 Hz and 58.5 Hz Standard UFLS Stages but shall not overlap with the load utilized to meet the 59.3 Hz Standard UFLS Stage.

(4)	Additional under-frequency relays may be installed on Transmission Facilities with the approval of ERCOT provided the relays are set at 58.0 Hz or below, are not directional, and have at least 2.0 seconds time delay.  A DSP may by mutual agreement arrange to have all or part of its automatic Load shedding requirement performed by another entity.  ERCOT will be notified and provided with the details of any such arrangement prior to implementation.

(5)	DSPs shall ensure, to the extent possible, and under the direction of ERCOT, that Loads equipped with under-frequency relays are dispersed geographically throughout the ERCOT Region to minimize the impact of Load shedding within a given geographical area.  Customers equipped with under-frequency relays shall be dispersed without regard to which Load Serving Entity (LSE) serves the customer.  DSPs shall ensure that Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs) are connected to circuits that are not subject to disconnection during UFLS events, except as permitted by Protocol Section 3.8.6, Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs).  DSPs shall ensure that the under-frequency relays connected to each Load will operate with a fixed time delay as specified in Tables (1) and (2) of paragraph (1) above.  Total time from the time when frequency first reaches one of the values specified above to the time Load is interrupted should be no more than the fixed time delay specified in Tables (1) and (2) of paragraph (1) above plus 10 cycles, including all relay and breaker operating times.  If the frequency drops below 58.5 Hz, ERCOT shall determine additional steps to continue operation.

(6)	If a loss of Load occurs due to the operation of under-frequency relays, a DSP or its designee may rotate the physical Load interrupted to minimize the duration of interruption experienced by individual Customers or to restore the availability of under-frequency Load-shedding capability.  In no event shall the initial total amount of Load without service be decreased without the approval of ERCOT.  TOs, in coordination with DSPs, shall make every reasonable attempt to restore Load, either by automatic or manual means, to preserve system integrity.  Restoration of any Load shed by UFLS systems, including Supplemental Kicker/Anti-Stall UFLS Load, shall be coordinated with ERCOT by the TO.  In the event frequency drops below any of the frequency thresholds specified in the tables in paragraph (1) above, and a TO’s UFLS relays that previously activated as a result of reaching that same frequency threshold have not been restored since the previous excursion, the Load on the feeders controlled by those relays shall be counted toward the TO’s satisfaction of the percentages in paragraph (1) above for that subsequent frequency excursion.