## Slide 1
ERCOT Frequency Control Report
July 2022
ERCOT
Operations Planning
PDCWG | Aug 17th, 2022

## Slide 2: Summary of July 2022
CPS1: 169.69%
Current CPS1 12-Month Rolling Average: 172.50%
0 BAAL Exceedance(s)
7 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2022 RMS1 Statistics
  Mean: 15.58 mHz
  Min: 12.43 mHz
  Max: 19.70 mHz
Energy Statistics
  Total Energy: 45,993,543 MWh
  Wind Energy: 8,753,431 MWh
  Percent Energy from Wind: 19.03 %
  Solar Energy: 2,937,875 MWh
  Percent Energy from Solar: 6.39%
Minimum System Inertia
  Mean: 288,716 MW*s
  Max: 344,003 MW*s on July 11th
  Min: 245,198 MW*s on July 2nd
Notes: Mean: 288,716 MW*s
Max: 344,003 MW*s on July 11th
Min: 245,198 MW*s on July 2nd

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
July-22 CPS1 (%): 169.69
Notes: 1. 85.59%@ 7/5/2022 HE 18:00
Expected Generation Deviation
Between 17:00-18:00 the Expected gen dev remained negative. The largest expected gen dev was -2459MW @ 5:23 PM with signification contribution from solar and wind generation.
IRR Ramps
Between 17:00-18:00 wind ramped down by ~2600 MW
Regulation: Regulation up was exhausted for most part of this hour. A manual SCED offset of 350 MW was applied.
2. 85.77% @ 7/9/2022 HE 16:00
Expected Generation Deviation
Expected generation deviation remained negative during most part of the hour. The largest expected gen dev was -541MW @ 4:40 PM with significant contribution from solar and thermal generation.
IRR Ramps
Between 4:05pm to 4:40 pm solar ramped down by ~700 MW.
One thermal unit was derated due to equipment issues.
Regulation: Regulation up was exhausted during the low expected gen dev periods.
3. 71.83%@ 7/12/2022 HE 21:00
Expected Generation Deviation
Between 20:00-21:00 the Expected gen dev remained negative. The largest expected gen dev was -1522MW @ 8:05 PM with signification contribution from solar and wind generation.
IRR Ramps
Between 20:00-21:00 wind ramped down by ~1100 MW
Between 20:00-21:00 solar ramped down by ~1700 MW
Regulation: Regulation up was exhausted for over half of this hour. Two manual SCED offsets of 300 and 200 MW were applied.
4. 49.81%@ 7/13/2022 HE 16:00
Expected Generation Deviation
Between 15:00-16:00 the Expected gen dev remained negative for most part of the hour. The largest expected gen dev was -2119MW @ 3:23 PM with signification contribution from solar generation.
IRR Ramps
Between 15:00-15:23 solar ramped down by ~800 MW
Between 15:50-16:00 solar ramped down by ~700 MW
Regulation: Regulation up was exhausted during the IRR ramping periods.
5. 84.20%@ 7/19/2022 HE 19:00
Expected Generation Deviation
Between 18:00-19:00 the Expected gen dev remained negative for most part of the hour. The largest expected gen dev was -2052MW @ 6:20 PM with signification contribution from solar and wind generation.
IRR Ramps
Between 18:05-18:20 wind ramped down by ~300 MW
Between 18:00-19:00 solar ramped down by ~2800 MW
Regulation: Regulation up was exhausted during the IRR ramping periods. Two manual SCED offsets of 300 and 500 MW were applied.
6. 75.90%@ 7/20/2022 HE 20:00
Expected Generation Deviation
Between 18:00-19:00 the Expected gen dev remained negative for the entire hour. The largest expected gen dev was -1971MW @ 7:30 PM with signification contribution from solar generation.
IRR Ramps
Between 19:00-20:00 solar ramped down by ~4000 MW
Regulation: Regulation up was exhausted for most part of this hour. A manual SCED offset of 300 MW was applied.
7. 36.92%@ 7/26/2022 HE 20:00
Expected Generation Deviation
Between 18:00-19:00 the Expected gen dev remained negative for the entire hour. The largest expected gen dev was -2968MW @ 7:32 PM with signification contribution from solar and wind generation.
IRR Ramps
Between 19:00-20:00 solar ramped down by ~4700MW
Regulation: Regulation up was exhausted for most part of this hour. Multiple SCED offsets were applied with the max offset of 400 MW.

## Slide 5: BAAL Exceedances & Violations
There are 0 BAAL exceedance(s) in July.

## Slide 6: 15-Minute Average CPS1%
July-22 CPS1 (%): 169.69
Notes: Overall the 15 min CPS1 score is above 160, Between 19:00 and 20:00 ,the CPS1 is between 110 to 150 due to solar down ramps.

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 172.50%
Notes: 12 month rolling average CPS1 score is 172.50, which is good and CPS1 score for July is slightly lower than the last month.

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year is so far slightly smaller overall compared with the 2021.
  Mean: 15.58 mHz
  Min: 12.43 mHz
  Max: 19.7 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by month
16.48Mhz on avg for July 2022

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Same data but only showing for the last 10 years

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison
Notes: Comparison of frequency profile for July 2021 and July 2022, we see slightly more instances of frequency hovering at or below the lower deadband in July 2022.

## Slide 13: Frequency Profile Comparison
Notes: Comparison of frequency profile for July 2020 and July 2022, same observation here, we see slightly more instances of frequency hovering at or below the lower deadband in July 2022.

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error
Notes: We did not make time error corrections. The drop in time error was due to significant IRR ramps. By making GTBD changes, we were able to successfully recover time error.

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 45,993,543 MWh
There is an increase in total energy compared to last year and last month

## Slide 22: Total Energy from Wind Generation
Notes: 8,753,431 MWh
We see notable decrease in the wind energy production in July.

## Slide 23: % Energy from Wind Generation
Notes: 19.03%
of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 2,937,875 MWh
There is also a notable increase in solar energy production in July.

## Slide 25: % Energy from Solar Generation
Notes: 6.39% of total energy was provided by solar generation

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia =245,198 MW*s on 07/02/2022
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 288,716 MW*s
Max: 344,003 MW*s on July 11th
Min: 245,198 MW*s on July 2nd

## Slide 28: Questions?
Thank you!