## Slide 1
Resource Integration Topics
Jay Teixeira
ERCOT
Resource Integration Working Group
August 23, 2022

## Slide 2: Quarterly Stability Assessment (QSA)
Planning Guide 5.9
Next Deadline for QSA
If a GINR is not included in QSA, its Initial Synchronization date will be automatically delayed to the next quarter
All-Inclusive Generation Resource Initial Synchronization Date | Last Day for an IE to meet prerequisites as listed in paragraph (4) below | Completion of Quarterly Stability Assessment
Upcoming January, February, March | Prior August 1 | End of October
Upcoming April, May, June | Prior November 1 | End of January
Upcoming July, August, September | Prior February 1 | End of April
Upcoming October, November, December | Prior May 1 | End of July

## Slide 3: Quarterly Stability Assessment (QSA)
Planning Guide 5.9, Quarterly Stability Assessment
Issue’s seen in previous QSA’s
  10 day comment period for FIS
    Needs to be complete before QSA deadline
    TSPs need to plan for it
  Dynamic/PSCAD Model Review
    Dependent on FIS Stability study
    Need to meet PG 6.9 15 to 30 days prior to QSA deadline
PSSE Model Quality Test Required
PSCAD Model Quality Test and Unit Model Validation required
TSAT Model Required – If PSSE model is UDM, then TSAT model should be UDM

## Slide 7: Miscellaneous Resource Integration Information
Case to Use for Screening and Full Interconnect Studies
  ERCOT changing summer cutoff from June 1 to July 1
  Align with SSWG cases
Staffing Issues
  Pause on processing periodic reactive and AVR tests
  Resume when fully staffed

## Slide 8: Screening Studies for Simultaneous GIM/FIS Applications
Planning Guide 5.3.1, Security Screening Study
5.3.1 Security Screening Study
(1) For each Generator Interconnection or Modification (GIM) submitted for a large generator, ERCOT will conduct a steady-state Security Screening Study, including power-flow and transfer studies, based on the expected in-service year to identify potential generation dispatch limitations based on the site proposed by the Interconnecting Entity (IE).
(a) The Security Screening Study is a high-level review of the project and generally includes a number of initial assumptions from both ERCOT and the IE. In accordance with P.U.C. Subst. R. 25.198, Initiating Transmission Service, ERCOT will establish the scope of the Security Screening Study that will include a determination of the need for a more in-depth Subsynchronous Resonance (SSR) study. The SSR vulnerability of all Generation Resources applicable under Section 5, Generator Interconnection or Modification, will be assessed pursuant to Protocol Section 3.22.1.2, Generation Resource or Energy Storage Resource Interconnection Assessment.
(b) At its sole discretion, ERCOT may waive the requirement for a Security Screening Study for a GIM.
ERCOT has created a Screening Study Template that states the Screening Study has been waived and includes a determination of the need for a SSR study.

## Slide 9: 4 Quadrant Telemetry Check for ESR
4-quadrant BESS unit telemetry check
  Completed before approval to lift the 20 MVA limit for transmission connected BESS units or before Part 3 testing for DESRs
  ERCOT will observe a check of the telemetry that demonstrates that it is functioning correctly during a 4-quadrant telemetry check for each of the BESS (battery) units at the station.
  The amount of BESS unit charging and discharging and leading and lagging reactive power can be small, around 2 - 5 MW and MVAr (or less for DESRs).
  All BESS unit Reactive Power needs to be shown on the generating unit gross and net MVAr telemetry with zero on the charging load MVAr telemetry, regardless of whether the BESS unit is charging or discharging.

## Slide 10: 4 Quadrant Telemetry Check for ESR
BESS unit discharging MW (shown as positive generator gross and net MW) and exporting MVAr (shown as positive generator gross and net MVAr)
BESS unit discharging MW (shown as positive generator gross and net MW) and importing MVAr (shown as negative generator gross and net MVAr)
BESS unit charging MW (shown as positive charging load MW and Load Resource NPF) and importing MVAr (shown as negative generator gross and net MVAr)
BESS unit charging MW (shown as positive charging load MW and Load Resource NPF) and exporting MVAr (shown as positive generator gross and net MVAr)
MW
MVAR
0 MW
0 Mvar
+ MW
+ GMV
0 MW
0 Mvar
+ MW
- GMV
0 MW
+ GMV
+ MW
0 Mvar
+ MW
0 Mvar
0 MW
- GMV

## Slide 11: Active RR’s
None

## Slide 12: Other contact information
ResourceIntegrationDepartment@ercot.com is distribution list for Resource Integration department
Mailing List
  RESOURCE_INTEGRATION@LISTS.ERCOT.COM

## Slide 13: Questions?
Thank you!