## Slide 1
Proposed Dispatchable/Flexible Resource Adequacy Measures for the CDR
Pete Warnken
Resource Adequacy Dept.
August 29, 2022
Notes: Welcome to

## Slide 2: Rationale for Additional Reserve Margin Measures
The current Planning Reserve Margin does not adequately capture the risk of Intermittent Renewable Resource (IRR) availability, including risks for hours other than the forecasted peak load hour
ERCOT is proposing to report PRMs for multiple hours to capture the “net load” implications of IRR capacity
However, additional PRM measures that focus on adequacy of non-IRR resources to address extreme net load risks are needed
  Is there sufficient dispatchable resource capacity available to cover the expected IRR tail risk (worst-case net load scenario) for the next several years?
  Is there sufficient flexible resource capacity available to cover expected extreme net load ramping requirements for the next several years?

## Slide 3: Dispatchable Resource Margin
Proposed Measure Purpose: Determine if the ERCOT region is expected to have sufficient dispatchable capacity to cover an extreme hourly net load scenario for a given forecast season and year
  Separate measures for blocks of the highest-risk hours for each season (“risk periods”)
  Use historical weather-year wind/solar profiles (scaled up to reflect planned resources) and load forecasts to determine the maximum firm net load for each risk period
  Develop a forecast of available “fully dispatchable” resource capacity for the annual/seasonal time periods
  The percentage measure for year y, season s, and risk period p is:
    100 x [(Dispatchable Capacityy,s,p / Extreme Firm Net Loady,s,p ) – 1]
  Dispatchable capacity deemed adequate if the margin is equal to or greater than 0%

## Slide 4: Dispatchable Resource Margin – Sample Summer Calc
Fully Dispatchable Resources: Those operational and planned units represented (or are expected to be represented) in ERCOT's Security Constrained Economic Dispatch (SCED) system that can increase or lower output in response to ERCOT instructions. This category includes coal, gas, nuclear, energy storage, hydroelectric, and other thermal resources.

## Slide 5: Flexible Resource Margin
Proposed Measure Purpose: Determine if the ERCOT region is expected to have sufficient flexible capacity to cover extreme net load up-ramp requirements for a given forecast season and year
  Separate measures for blocks of the highest-risk hours for each season (“risk period”)
  Develop projected net load up-ramp requirements for each risk period using historical one-minute data as the starting point
    Maximum net load up-ramp seen during the defined risk period; e.g., for a two-hour risk period, each up-ramp is Net Loadm+120 - Net Loadm, where m is the starting minute for the up-ramp calculation. Calculations would be for two-hour moving windows, beginning at two hours prior to the start of the risk period and ending at two hours after the end of the risk period.
  The percentage measure for year y, season s, and risk period p is:
    100 x [(Flexible Capacityy,s,p / Net Load Up-ramp Requirementy,s,p ) – 1]
  Flexible capacity deemed adequate if the margin is equal to or greater than 0%

## Slide 6: Dispatchable Resource Margin – Summer Example
Flexible Resources: The seasonal net maximum sustained ratings for Fully Dispatchable operational and planned resources that meet or exceed the following operational parameter values: (1) Cold start time of less than or equal to two hours, and (2) Minimum On-Line Time of less than or equal to two hours. These resources generally include the following types: (1) combustion turbines, (2) internal combustion engines, (3) energy storage, and (4) hydroelectric with reservoir storage.
Example “Flexible Resource” Definition

## Slide 7: Combined Measure Mock-up (Summer)

## Slide 8: Questions
?
Pete Warnken
Pete.Warnken@ercot.com