## Slide 1
PDCWG Report to ROS
Chair: Jimmy Jackson, CPS
Vice Chair: Vacant
ROS
Sep 1st, 2022

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs and IMFR
    1 FME in the month of July
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 8/17/2022
  ECRS Deployment and Requirement Methodology
  RRS Limit Study Update
  ERCOT Reports
  TRE Report

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 1 FME in July
  7/27/2022 1:17:48
    Loss of 517 MW of generation
    Interconnection Frequency Response: 1,326 MW/0.1 Hz
    80 Resources were evaluated. These includes,
      34 Generation Resources
      2 Controllable Load Resources
      44 Energy Storage Resources
    7 of 80 Evaluated Resources had less than 75% of their expected Initial Primary Frequency Response.
    13 of 80 Evaluated Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 412 MW/0.1 Hz
IMFR Performance currently
1223.77 MW/0.1HZ

## Slide 7
Questions?

## Slide 8: Frequency Control Report
July 2022

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency
Notes: 16.48Mhz on avg for July 2022

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections
Notes: Time error started to go down around the 7th due to significant IRR ramps and heatwave. Several GTBD changes were made later in the month to recover time error.

## Slide 13: ERCOT Total Energy
Notes: 45,993,543 MWh

## Slide 14: ERCOT Total Energy from Wind Generation
Notes: 8,753,431 MWh

## Slide 15: ERCOT % Energy from Wind Generation
Notes: 19.03%

## Slide 16: ERCOT Total Energy from Solar Generation
Notes: 2,937,875 MWh

## Slide 17: ERCOT % Energy from Solar Generation
Notes: 6.39%