## Slide 1
ERCOT Frequency Control Report
August 2022
ERCOT
Operations Planning
PDCWG | Sep 14th, 2022

## Slide 2: Summary of August 2022
CPS1: 170.85%
Current CPS1 12-Month Rolling Average: 172.21%
1 BAAL Exceedance(s)
0 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2022 RMS1 Statistics
  Mean: 15.66 mHz
  Min: 12.43 mHz
  Max: 19.70 mHz
Energy Statistics
  Total Energy: 43,067,150 MWh
  Wind Energy: 6,279,388 MWh
  Percent Energy from Wind: 14.58 %
  Solar Energy: 2,374,549 MWh
  Percent Energy from Solar: 5.51%
Minimum System Inertia
  Mean: 295,241 MW*s
  Max: 333,523 MW*s on Aug 11th
  Min: 246,162 MW*s on Aug 28th
Notes: Mean: 295,241 MW*s
Max: 333,523 MW*s on Aug 10th
Min: 246,162 MW*s on Aug 28th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Aug-22 CPS1 (%): 170.85

## Slide 5: BAAL Exceedances & Violations
There is 1 BAAL exceedance(s) in August.
Notes: Occurred on 8/21/2022 due to a gen loss event (8/21/2022 19:27:02)

## Slide 6: 15-Minute Average CPS1%
Aug-22 CPS1 (%): 170.85

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 172.21%
Notes: 12 month rolling average CPS1 score is 172.21, which is good and CPS1 score for Aug is slightly higher than the last month.

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year is so far slightly smaller overall compared with the 2021.
  Mean: 15.66 mHz
  Min: 12.43 mHz
  Max: 19.7 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by month
16.17Mhz on avg for August 2022

## Slide 10: Daily RMS1 of ERCOT Frequency by Month

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 43,067,150 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,279,388 MWh

## Slide 23: % Energy from Wind Generation
Notes: 14.58%
of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 2,374,549 MWh

## Slide 25: % Energy from Solar Generation
Notes: 5.51% of total energy was provided by solar generation

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia =246,162 MW*s on 08/28/2022
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 295,241 MW*s
Max: 333,523 MW*s on Aug 10th
Min: 246,162 MW*s on Aug 28th

## Slide 28: Questions?
Thank you!