## Slide 1
Refresher on Jointly-Rated Branches
9/19/2022

## Slide 2: Topics
Terminology
Incorporating Limiting Elements in Branch Ratings
Jointly-Rated Branches
Jointly-Rated Complications
Key Takeaways

## Slide 3: Terminology for This Presentation
Jointly-Rated Branch
  Line or transformer with more than one company providing ratings
Jointly-Owned Branch
  Line or transformer which has ownership associations to more than one company
  Ownership, in this discussion, refers to the mechanism giving permissions to the data instance. Associated “owners” of the data instance can provide ratings.
A line must have multiple ownership associations in order to have multiple ratings sets

## Slide 4: Branch Ratings as a Proxy for Other Equipment Ratings
ERCOT systems only consider ratings on lines and transformers when performing analysis
As such, applicable limiting equipment ratings must be “baked into” the line and transformer ratings
NDSWG Meeting Notes, ROS 8/11/2005
https://www.ercot.com/calendar/event?id=1421263490400
Reporting pulled from archival microfiche

## Slide 5
Devices within the green box are part of the facility.
SUBB
SUBA
A_B_1
700 MVA
CBA1 478 MVA
CBB1 478 MVA
DSCB1 478 MVA
DSCB2 478 MVA
DSCA2 478 MVA
Buswork 287
MVA
Buswork478
MVA
PT
478 MVA
PT
478
MVA
WT
478 MVA
WT
478 MVA
DSCA1 478 MVA
Example #1 – Equipment Ratings Incorporated in Facility Rating

## Slide 6: Example #1 – Equipment Ratings Incorporated in Facility Rating
Substation A
  Buswork – 287 MVA
  DSCA1 – 478 MVA
  CBA1 – 478 MVA
  PT – 478 MVA
  DSCA2 – 478 MVA
  WT – 478 MVA
Substation B
  Buswork – 478 MVA
  DSCA1 – 478 MVA
  CBA1 – 478 MVA
  PT – 478 MVA
  DSCA2 – 478 MVA
  WT – 478 MVA
Line - A_B_1
  700 MVA
SUBB
SUBA
A_B_1
700 MVA
CBA1 478 MVA
CBB1 478 MVA
DSCB1 478 MVA
DSCB2 478 MVA
DSCA2 478 MVA
Buswork 287
MVA
Buswork478
MVA
PT
478 MVA
PT
478
MVA
WT
478 MVA
WT
478 MVA
DSCA1 478 MVA

## Slide 7: Jointly-Rated Branches
An individual branch can have separate ratings for each company that is denoted as an “owner”
One OwnerShareRating Per Company
Multiple Ownership associations
Downstream systems will use the most conservative value per rating type and temperature

## Slide 8: An OwnerShareRating (OSR) for Each Company
Jointly-rated lines should have an OwnerShareRating (OSR) for each company
Static ratings are required but dynamic ratings are optional
ERCOT applications will extend static-only OSR values across all temperatures when paired with a dynamically rated OSR

## Slide 9: Example #2 – Jointly-Rated Facility
Assuming the boxed devices are the facility.
Determine the Normal Rating for the Static Rating for each Company.
Company X Owned
Company Y Owned
SUBB
SUBA
A_B_1
700 MVA
CBA1 478 MVA
CBB1 478 MVA
DSCB1 478 MVA
DSCB2 478 MVA
DSCA2 478 MVA
Buswork 478
MVA
Buswork478
MVA
PT
478 MVA
PT
191
MVA
WT
478 MVA
WT
478 MVA
DSCA1 478 MVA

## Slide 10: Example #2 – Jointly-Rated Facility
Company X Normal Rating
  Buswork – 478 MVA
  DSCA1 – 478 MVA
  CBA1 – 478 MVA
  PT – 478 MVA
  DSCA2 – 478 MVA
  WT – 478 MVA
  Line – 700 MVA
  Normal Rating: 478 MVA
Company Y Normal Rating
  Buswork – 478 MVA
  DSCB1 – 478 MVA
  CBB1 – 478 MVA
  PT – 191 MVA
  DSCB2 – 478 MVA
  WT – 478 MVA
  Line – 700 MVA
  Normal Rating: 191 MVA
Company X Owned
Company Y Owned
SUBB
SUBA
A_B_1
700 MVA
CBA1 478 MVA
CBB1 478 MVA
DSCB1 478 MVA
DSCB2 478 MVA
DSCA2 478 MVA
Buswork 478
MVA
Buswork 478
MVA
PT
478 MVA
PT
191
MVA
WT
478 MVA
WT
478 MVA
DSCA1 478 MVA

## Slide 11: Example #3 – Jointly-Rated Facility
Assuming the boxed devices are the facility.
Assuming 138 kV operating voltage.
Determine the Normal Rating for the Static Rating for each Company.
Company X Owned
Company Y Owned
SUBB
SUBA
A_B_1
700 MVA
CBA1 717 MVA
CBB1 717 MVA
DSCB1 717 MVA
DSCB2 717 MVA
DSCA2 717 MVA
Buswork 717
MVA
Buswork717
MVA
PT
717 MVA
PT
717
MVA
WT
717 MVA
WT
717 MVA
DSCA1 478 MVA

## Slide 12: Example #3 – Jointly-Rated Facility
Company X Normal Rating
  Buswork – 717 MVA
  DSCA1 – 478 MVA
  CBA1 – 717 MVA
  PT – 717 MVA
  DSCA2 – 717 MVA
  WT – 717 MVA
  Normal Rating: 478 MVA
Company Y Normal Rating
  Buswork – 717 MVA
  DSCB1 – 717 MVA
  CBB1 – 717 MVA
  PT – 717 MVA
  DSCB2 – 717 MVA
  WT – 717 MVA
  Line – 700 MVA
  Normal Rating: 700 MVA
Company X Owned
Company Y Owned
SUBB
SUBA
A_B_1
700 MVA
CBA1 717 MVA
CBB1 717 MVA
DSCB1 717 MVA
DSCB2 717 MVA
DSCA2 717 MVA
Buswork 717
MVA
Buswork717
MVA
PT
717 MVA
PT
717
MVA
WT
717 MVA
WT
717 MVA
DSCA1 478 MVA

## Slide 13: Jointly-Rated Complications
It can be difficult to identify – and then keep up to date – all scenarios where your equipment interfaces with another company’s equipment
Ratings change over time due to equipment upgrades and methodology adjustments
  Did the CR submitted by your neighbor just make your equipment limiting?
What other complications are there?

## Slide 14: Key Takeaways
Branch ratings must consider all equipment ratings from “bus to bus”
  Companies must provide an OSR incorporating the ratings for their equipment following their Ratings Methodology
  Multiple companies must provide OSRs when ownership changes occur along or at the ends of a facility
A company should submit an OSR whenever their equipment’s ratings must be considered (although it may not currently be limiting) for the facility rating
Interfacing companies must coordinate to ensure all equipment is considered in the provided OSRs
Interfacing companies should not, as a practice, provide matching OSRs
  OSRs should be submitted with values determined by each company’s Ratings Methodology
Interfacing companies must coordinate to ensure OSRs are reevaluated when CRs, representing the end of a project, are submitted to ERCOT
OSR (OwnerShareRating) = An individual company’s ratings set

## Slide 15: Appendix

## Slide 16: SCR813 - Submitter Shown Jointly-Rated Equipment and Coordination Confirmation Requested

## Slide 17: SCR813 - Enhanced Notifications – “Walking the Tree”
Add functionality to send notifications to model-instance owners when “nearby” changes are made.
Currently notifications are only sent to owners of modified instances
Ratings sets are only owned by one company
  Each company will have their own ratings set if jointly owned
Example
  A notification would be sent to Company B if Ratings Set #1 were modified by Company A
Changing the impedance will send a notification to Company A and Company B
Changing the ratings in Ratings Set #1 will only send a notification to Company A
Changing the ratings in Ratings Set #1 will only send a notification to Company B

## Slide 18: SCR813 - Additional Notification
The notification currently sent when a NOMCR is submitted would also be sent to all associated companies