| NPRR Number | 1144 | NPRR Title | Station Service Backup Power Metering |
| --- | --- | --- | --- |
| Date |  | August 17, 2022 |  |
| Submitter’s Information |  |  |  |
| Name |  | Ann Coultas; Ravi Beeravalli |  |
| E-mail Address |  | ann.coultas@enel.com; rbeeravalli@pluspower.com |  |
| Company |  | Enel Green Power North America, Inc.; Plus Power (Joint Commenters) |  |
| Phone Number |  | (978) 773-0739; (218) 387-4538 |  |
| Cell Number |  |  |  |
| Market Segment |  | Independent Generator; Not Applicable |  |

Comments

Enel Green Power North America, Inc. (Enel) appreciates Plus Power filing this Nodal Protocol Revision Request (NPRR) to address an issue that is important to increase reliability of the ERCOT grid.  Enel and Plus Power (Joint Commenters) also appreciate the comments ERCOT filed on the original proposal and file these additional comments to address issues raised therein.

Continuity of electrical power to a Generation Resource’s auxiliary Load, including station service, is important to ensure reliable communications, security, and possibly the protection scheme of a substation.  Under current practices, a dedicated standby generator is generally used for redundant power supply to this load.  These generators can be less reliable and sustainable in comparison to distribution service.  Allowing auxiliary Load to receive power from the distribution grid in an emergency and during brief periods for maintenance would provide an additional means to ensure reliable electricity supply to this auxiliary Load.  To clarify that this NPRR is not intended to change or impact the metering requirements or determination of Wholesale Storage Load (WSL), the language originally proposed to be inserted in paragraph (3)(a)(ii) of Section 10.3.2.3, Generation Netting for ERCOT-Polled Settlement Meters, has been deleted.

The changes proposed in these comments achieve the same practical result as originally proposed by Plus Power but provide clarity as to the nature of the electrical connection to allow emergency service from the distribution grid, ensure agreement of affected stakeholders necessary to allow this emergency service to be provided, and provide a clear standard to measure the maximum amount of auxiliary Load that can be served in these emergency situations.

Revised Cover Page Language

| - Requested Resolution | - Normal |
| --- | --- |
| - Revision Description | - This Nodal Protocol Revision Request (NPRR) provides a limited exception to the requirement that all loads included in the netting arrangement for an ERCOT-Polled Settlement (EPS) Metering Facility only be connected to the ERCOT Transmission Grid through the EPS metering point(s) for the Facility. The exception would allow no more than 500kW of auxiliary Load connected to a station service transformer to be connected to a Transmission Service Provider’s (TSP’s) or Distribution Service Provider’s (DSP’s) Facilities through a separately metered point using an open transition load transfer switch listed for emergency use. |
| - Business Case | - Allowing the relatively insignificant load of backup station service in emergency and maintenance situations to be provided and metered by the DSP and/or alternate connection to the TSP would allow generators to eliminate the need for an on-site backup generator which has initial high costs and continued maintenance costs. It also requires a fuel source that would likely require further local permitting. Eliminating fuel storage also makes the site inherently safer. - A meter that has the capability to function as an EPS Meter is also not a standard meter for most local distribution companies and the requirement of an EPS Meter would mean additional infrastructure to support the backup service. |

Revised Proposed Protocol Language

- 10.3.2.3	Generation Netting for ERCOT-Polled Settlement Meters

(1)	Each Generation Resource and Settlement Only Generator (SOG) and each Load that is designated to be netted with that Generation Resource or SOG, including construction and maintenance Load that is netted with existing generation auxiliaries, must be physically metered at its POI to the ERCOT Transmission Grid or Service Delivery Point, or, in accordance with Section 10.3.2.2, Loss Compensation of EPS Meter Data, loss-compensated to its POI to the ERCOT Transmission Grid.  Interval Data Recorders (IDRs) must be used to determine generator output or Load usage.  In the intervals where the generation output exceeds the Load, the net must be settled as generation.  In the intervals where the Load exceeds the generation output, the net must be settled as Load, and carry any applicable Load shared charges and credits.

(2)	For Settlement purposes, netting is not allowed except under the configurations described in paragraphs (2)(a) through (2)(e) below, and only if the service arrangement is otherwise lawful.  ERCOT has no obligation to independently determine whether a site configuration that includes both Loads and Generation Resource(s) or SOGs complies with Public Utility Regulatory Act (PURA) or the Public Utility Commission of Texas (PUCT) Substantive Rules, and ERCOT’s approval of a metering proposal for such a site is not a verification of the legality of that arrangement:

(a)	Single POI or Service Delivery Point;

(b)	Transmission-level interconnections where all POIs are located at the same substation, at the same voltage, and under normal operating conditions, are interconnected through common electrical equipment such as circuit breakers, connecting cables, bus bars, switches/isolators.  Qualifying station arrangements include, but are not limited to, Generation and Load connected in a line bus, ring bus, double-breaker, or breaker-and-a-half configuration;

(c)	Multiple POIs where the Loads and generator output are electrically connected to a common switchyard, as defined in paragraph (7) below.  In addition, there must be sufficient generator capacity to serve all plant Loads for netting to occur;

(d)	A Qualifying Facility (QF) with POIs, where the QF is selling energy to a thermal host, may net the Load meters of the thermal host with the QF’s generation meters when the Load and generation are electrically connected to a common switchyard.  In instances in which Load is served by new on-site generation through a common switchyard, the TSP or DSP may install monitoring equipment necessary for measuring Load to determine stranded cost charges, if any are applicable, as determined under the PURA and applicable PUCT rules.  For purposes of this Section, new on-site generation has the meaning as contained in Public Utility Regulatory Act, Tex. Util. Code Ann. §§ 39.252 and 39.262(k) (Vernon 1998 & Supp. 2007) (PURA); or

(e)	For Generation Resources and/or Load with flow-through on a private, contiguous transmission system (not included in a TSP or DSP rate base) and in a configuration existing as of October 1, 2000, the meters at the interconnections with the ERCOT Transmission Grid may be netted for the purpose of determining Generation Resources or Load.  For Settlement purposes, when the net is a Load, the metered interconnection points must be assigned to the same Load Zone and Unaccounted for Energy (UFE) zone.

(3)	For Energy Storage Resource (ESR) sites, Wholesale Storage Load (WSL) must be separately metered from all other Loads and generation, and must be metered using EPS Metering Facilities.

(a)	For configurations where the Resource Entity telemeters an auxiliary Load value to the EPS Meter:

(i)	The total energy into the ESR must be separately metered from all other Loads and generation, and must be metered using EPS Metering Facilities; and

(ii)	The auxiliary Load energy shall be stored in the EPS Meter’s IDR, per channel assignments defined in the SMOG.

(b)	For configurations where the WSL is not at a POI, it must be metered behind a single POI metering point, per the requirements in paragraph (3) or (3)(a) above; and

(c)	WSL for a compressed air energy storage Load Resource is exempt from the requirement to be electrically connected to a common switchyard, as defined in paragraph (7) below.

[NPRR995: Replace paragraph (3) above with the following upon system implementation:] (3) For Energy Storage Resource (ESR), Settlement Only Distribution Energy Storage System (SODESS), or Settlement Only Transmission Energy Storage System (SOTESS) sites, Wholesale Storage Load (WSL) must be separately metered from all other Loads and generation, and must be metered using EPS Metering Facilities. (a) For configurations where the Resource Entity telemeters an auxiliary Load value to the EPS Meter: (i) The total energy into the ESR, SODESS, or SOTESS must be separately metered from all other Loads and generation, and must be metered using EPS Metering Facilities; and (ii) The auxiliary Load energy shall be stored in the EPS Meter’s IDR, per channel assignments defined in the SMOG. (b) For configurations where the WSL is not at a POI, it must be metered behind a single POI metering point, per the requirements in paragraph (3) or (3)(a) above; and (c) WSL for a compressed air energy storage Load Resource is exempt from the requirement to be electrically connected to a common switchyard, as defined in paragraph (7) below.

(4)	ERCOT shall maintain descriptions of the Metering Facilities of all common switchyards that contain multiple POIs of Loads (ESI IDs) and generation meters (EPS).  The description is limited to identifying the Entities within a common switchyard and a simplified diagram showing the metering configuration of all Supervisory Control and Data Acquisition (SCADA) and Settlement Metering points.

(5)	All Load(s) included in the netting arrangement for an EPS Metering Facility shall only be electrically connected to the ERCOT Transmission Grid through the EPS metering point(s) for such Facility.  Such Loads shall not be electrically connected to the ERCOT Transmission Grid through electrical connections that are not metered by the EPS metering point(s) for the Facility.

(6)	Notwithstanding the requirements of paragraph (5) above, auxiliary Load(s) connected to the station service transformer not to exceed 500 kW in aggregate shall be permitted an additional electrical connection to a TSP’s or DSP’s Facilities through a separately metered Transmission and/or Distribution Service Provider (TDSP) read metering point.  This configuration requires mutual agreement between a TSP, DSP, and Resource Entity, and the connection shall be achieved through an open transition load transfer switch listed for emergency service and shall only be used in emergency and maintenance situations.

(7)	For purposes of this Section, a common switchyard is defined as an electric substation Facility where the POI for Load and Generation Resources are located at the same Facility but where the interconnection points are physically not greater than 400 yards apart.  The physical connections of the Load to its POI and the Generation Resource to its POI cannot be Facilities that have been placed in a TSP’s or DSP’s rate base.

(8)	Notwithstanding any other provision in this section, for any Generation Resource or ESR that is configured to serve a Customer Load as part of a Private Microgrid Island (PMI), the connection to the Customer Load in the PMI configuration shall be located behind the EPS metering point at the Resource’s POI.  For a PMI configuration that includes an ESR that is receiving WSL treatment for charging Load, an EPS Meter shall be located to measure the ESR’s gross output net of any internal telemetered auxiliary Load, and a separate TDSP ESI ID (for nodal Settlement) with a Load Serving Entity (LSE) association must be established for the site prior to service of any Load.

[NPRR945: Insert paragraph (9) below upon system implementation:] (9) ERCOT shall post on the ERCOT website a report listing all Generation Resources or Settlement Only Generators (SOGs) that have achieved commercial operations, excluding Decommissioned Generation Resources, Mothballed Generation Resources, and decommissioned SOGs, whose Resource Registration data indicates that the Generation Resource or SOG is part of a Private Use Network. The report must identify the name of the Generation Resource or SOG site, its nameplate capacity, and the date the Generation Resource or SOG was added to the report. The report shall not identify any confidential, customer-specific information regarding netted loads. ERCOT shall update the list at least monthly.