## Slide 1
Resource Integration Topics
Jay Teixeira
ERCOT
Resource Integration Working Group
October 20, 2022

## Slide 2: Quarterly Stability Assessment (QSA)
Planning Guide 5.9
Next Deadline for QSA
If a GINR is not included in QSA, its Initial Synchronization date will be automatically delayed to the next quarter
All-Inclusive Generation Resource Initial Synchronization Date | Last Day for an IE to meet prerequisites as listed in paragraph (4) below | Completion of Quarterly Stability Assessment
Upcoming January, February, March | Prior August 1 | End of October
Upcoming April, May, June | Prior November 1 | End of January
Upcoming July, August, September | Prior February 1 | End of April
Upcoming October, November, December | Prior May 1 | End of July

## Slide 3: Quarterly Stability Assessment (QSA)
Planning Guide 5.9, Quarterly Stability Assessment
Issue’s seen in previous QSA’s
  10 day comment period for FIS
    Needs to be complete before QSA deadline
    TSPs need to plan for it
  Dynamic/PSCAD Model Review
    Dependent on FIS Stability study
    Need to meet PG 6.9 15 to 30 days prior to QSA deadline
PSSE Model Quality Test Required
PSCAD Model Quality Test and Unit Model Validation required
TSAT Model Required – If PSSE model is UDM, then TSAT model should be UDM

## Slide 7: Submitted Questions
How do we calculate the required MVAR at the POI Bus? Is it based on the maximum net MW at the POI or the maximum net MW at the POI Bus? The reactive requirement at the POIB is based on the maximum net MW of the generating unit (i.e. does not include addition station load behind the POIB that is not part of the generating unit) that can be supplied at the POIB
Question for TSPs: Do TSPs provide the REs with line parameters of tie line?

## Slide 8: Submitted Questions
Since the number of PUN loads interconnecting behind the meter of the generation resources is increasing, what is ERCOT’s expectation in terms of how the project shall compensate for the reactive power consumed by the PUN Load? Can automatically switchable static VAr-capable devices be used to compensate for the reactive power consumed by the PUN loads OR only the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAr-capable devices are acceptable to compensate for the reactive power consumed by the PUN loads?
The load has an obligation to maintain a power factor of .97 or better, not considering any reactive capability required by the generator. Static reactive devices can be utilized to adjust to MVAR loading changes throughout the operating day to maintain this .97 power factor or better. Typically, the generating units required dynamic reactive capability at the POIB is preserved by its own shunts needed to compensate for voltage losses up to the POIB, so the total reactive needs must be coordinated to be met by the load and its reactive devices (.97 pf or better), the generator and its reactive capabilities (.95 lead/lag at the POIB + any supplemental to compensate for losses), and transmission operator supplied MVAR capability ( to serve the remaining MVAR load).

## Slide 9: Submitted Questions
Inclusion of DYR, raw file or other current model data in RIOO-RS and made accessible to RE. The RE desire is to be able to see model data as it currently exists and all attachments at anytime. This will be included early next year in RIOO-RS.

## Slide 10: VSS Requirement
NPRR1005-Clarifying the definition of POI and POIB was implemented on Feb 1st, 2022.
Nodal Protocol 2- Point of Interconnection Bus (POIB):
  Electric Bus at the TSP substation that is electrically closest to the Generation Resource’s POI or any electrically equivalent Electrical Bus at that station.
Nodal Protocol 3.15 (4): VSS requirement is at the POIB.
  Reactive Study should account for the gen-tie line regardless of ownership.
  Part 3 Test: VSS requirement is calculated at the POIB.

## Slide 11: Part 3 Tests: Co-located Resources behind the same POI
Reactive Test- Each Resource (solar, storage) is tested individually to meet requirement per NOG 3.3.2.2
VSS: Each Resource independently and combined must meet VSS per NP 3.15.
  Solar
  Storage
  Solar + Storage
AVR Test- Test three scenarios
  Solar
  Storage
    AVR test can be run at night.
  Solar + Storage: the combined test is to verify that the plant can control the voltage at the POIB with both Resources online.

## Slide 12: Active RR’s
None

## Slide 13: Other contact information
ResourceIntegrationDepartment@ercot.com is distribution list for Resource Integration department
Mailing List
  RESOURCE_INTEGRATION@LISTS.ERCOT.COM

## Slide 14: Questions?
Thank you!