## Slide 1
LFLTF: LFL-40, Load Shed Prior to EEA3
Jeff Billo
Operations Planning
October 24, 2022

## Slide 2: Background
Definition discussion at September 26, 2022 LFLTF meeting included proposed “Interruptible Load”
  In part, an Interruptible Load “can interrupt it’s load at a specified ramp rate when instructed by ERCOT for transmission issues or system capacity needs”
  https://www.ercot.com/files/docs/2022/09/26/092622%20LFL%20Defintions%20v2.pptx
LFL-40: Load shed prior to EEA3
Related LFLTF issues:
  LFL-33: Consider the impacts of and need for rules related to self-limiting RAS/CMPs
  LFL-35: Consider what changes to outage coordination processes are needed to incorporate LFL, including load assumptions for outage coordination studies
  LFL-38: To the degree certain LFLs are excluded from UFLS and/or firm load shed obligations, identify any processes necessary for curtailing/deploying those loads

## Slide 3: PRC Triggers in Scarcity Conditions (Existing)
3000 MW - Advisory
2500 MW - Watch
2300 MW - Energy Emergency Alert Level 1
1750 MW - Energy Emergency Alert Level 2
1000 MW - Energy Emergency Alert Level 3
3200 MW – Deploy Non-Spin

## Slide 4: PRC Triggers in Scarcity Conditions (Proposed)
3000 MW - Advisory
2500 MW - Watch
2300 MW - Energy Emergency Alert Level 1
1750 MW - Energy Emergency Alert Level 2
1000 MW - Energy Emergency Alert Level 3
3200 MW – Deploy Non-Spin
3200 MW – Interruptible Load

## Slide 5: Summarized Process for Deploying Interruptible Load During Scarcity Conditions
If PRC is <3200 and not expected to recover above 3200 within 30 minutes without additional actions:
  Deploy blocks of NSRS to stay above 3200
  Commit any available remaining offline generation
If after step 1, PRC is <3200 and not expected to recover above 3200 within 30 minutes without additional actions:
  Deploy blocks of Interruptible Load
If PRC is <3000 and not expected to recover above 3000 within 30 minutes without additional actions:
  Issue Advisory
  Confirm all available remaining offline generation is online
  Deploy ERS
  Deploy TO Distribution Voltage Reduction
…

## Slide 6: Interruptible Load Blocks
To avoid interrupting too much load at once, similar to Non-Spin Reserve Service, ERCOT would randomly group Interruptible Load into ~500 MW blocks
ERCOT would monitor actual consumption in real-time to maintain situational awareness of how much load is in each block
  ERCOT may shed more than one block at a time to achieve the reliability objective

## Slide 7: Other Thoughts
ERCOT does not envision shedding Interruptible Load to resolve transmission constraints except as a last resort during a transmission emergency, similar to the current treatment of Load Resources
ERCOT suggests using a term other than “Interruptible Load” as this is a NERC-defined term that may mean something different than intended in the context of LFLs

## Slide 8: Questions/ Comments