## Slide 1
Automatic UFLS Options for LFLTF discussion LFL-31 and LFL-38

## Slide 2: Goal
Simple Implementation
Implement UFLS Loadshed in similar fashion that operators have been trained on.
Ensure LFL are shed Automatically in steps aligned with Firm load UFLS.
Allow optional treatment for these loads but then based on this selection having clear rules.
Address complications for TO’s due to LFL being more responsive to market

## Slide 3: Approach/Concept for UFLS for LFLs
Require connecting Large Loads to register as either Firm/Native Load or LFL
Based on this selection apply UFLS rules
LFL loads would be required to install and maintain UFLS based on same settings as Firm/Native Load UFLS.
LFL loads would certify their UFLs and provide details to TSP and ERCOT when established or modified.
Notes: Simple Implementation
Implement Loadshed in similar fashion that operators have been trained on.
Ensure LFL are shed Automatically in steps aligned with Firm load UFLS.
Allow optional treatment for these loads but then based on this selection having clear rules.
Address complications for TO’s due to LFL being more responsive to market

## Slide 4: UFLS example on an LFL site
5800
6895
5000
5500
6000
6800
H
LD
-
1
LD
-
2
LD
-
3
LD
-
4
LD
-
5
LD-6
-
5%
UFLS
10%
UFLS
10%
UFLS
Total
25%
UFLS
Frequency Threshold | LFL Load Relief
59.3 Hz | At least 5% of the LFL Load
58.9 Hz | A total of at least 15% of the LFL Load
58.5 Hz | A total of at least 25% of the LFL Load
Notes: Simple Implementation
Implement Loadshed in similar fashion that operators have been trained on.
Ensure LFL are shed Automatically in steps aligned with Firm load UFLS.
Allow optional treatment for these loads but then based on this selection having clear rules.
Address complications for TO’s due to LFL being more responsive to market

## Slide 5: Requests
2 Options for Consideration:
LFL shares responsibility to shed load when grid conditions warrant:
  Design so that the load is not shed at the transmission level breaker
  ERCOT requires Load to shed in incremental steps on customer side (i.e., 5-10-10)
  For TO owned substations, TO owns and operates the UFLS or,
  For customer owned substations, Load owns the breakers and supplies TO with required testing records and compliance documentation.
  Allows Large Load to participate in AS with remaining site load.
Pass the entire obligation to the LFL for compliance (i.e., 5-10-10)
  The 5-10-10 is applicable to 25% of site load.
  Design so that the load is not shed at the transmission level breaker
  ERCOT will require P.E. attestation for correct installation of breakers provided to ERCOT and TO
  Allows Large Load to participate in AS with remaining site load.