## Slide 1
Oct 27, 2022 | OWG
ERCOT Staff
Proposed 2023 Ancillary Service Methodology And Preliminary Quantities

## Slide 2: Stakeholder Discussion Timeline
September 14, 2022 – PDCWG (Methodology Discussion)
September 23, 2022 – WMWG (Methodology Discussion)
October 20, 2022 – PDCWG (Proposed Methodology)(Rescheduled to Oct 28.)
October 21, 2022 – WMWG (Proposed Methodology)
October 27, 2022 – OWG (Proposed Methodology)
October 28, 2022 – PDCWG (Proposed Methodology)
November 02, 2022 - WMS
November 07, 2022 - ROS
December 5, 2022 - TAC
December 20, 2022 – BoD

## Slide 3: Discussion Scope for Today
This presentation will discuss the proposed methodology for computing Ancillary Service (A/S) quantities in 2023.
  ERCOT is not proposing any changes in the methodologies used to compute Regulation Service and Responsive Reserve Service (RRS) requirements for 2023.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2023 assessment for ERCOT shows an increase in ERCOT’s IFRO. With the update in ERCOT’s 2023 IFRO, minimum RRS-PFR limit for 2023 will change to 1,390 MW.
  ERCOT is proposing some changes in the methodology used to compute minimum Non-Spinning Reserve Service (Non-Spin) requirements in 2023. Specifically,
    Prior to ECRS: Use 85th to 95th percentile of 10 Hours Ahead (HA) max. net load forecast error
    After ECRS: Use 75th to 95th percentile of 6 HA hourly avg. net load forecast error
  Upon its implementation, ERCOT is proposing to compute ECRS requirements as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support sustained net load ramps.
The Ancillary Service (A/S) quantities for 2023 contained in this presentation are based on the methodology that was approved in December 2021.
  The quantities for 2023 reflect moving forward the historic data on which these are based, unless otherwise noted.
  Spreadsheets that contain the associated quantities have been posted on today’s meeting page.

## Slide 4: Regulation Service Methodology
ERCOT is not proposing any change to the methodology used to compute the minimum Regulation Service requirements in 2023.
The preliminary Regulation quantities for January 2023 through September 2023 in subsequent slides have been computed using current methodology (2021 and 2022 five-minute net load variability), updated Wind Adjustment tables and the updated Solar Adjustment tables.

## Slide 5: Hourly Average Regulation Comparison

## Slide 6: Responsive Reserve Service (RRS) Methodology
ERCOT is not proposing any changes to methodology used to compute the minimum RRS requirements for 2023.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2023 assessment for ERCOT shows an increase in ERCOT’s IFRO. With the update in ERCOT’s 2023 IFRO, minimum RRS-PFR limit for 2023 will change to 1,390 MW.
The preliminary RRS quantities for January 2023 through September 2023 in subsequent slides have been computed using 2021 and 2022 system inertia conditions and updated RRS table.
  The RRS table tracks RRS requirements for different inertia conditions. This table was updated in 2023 to use a minimum RRS-PFR limit of 1,390 MW.
Notes: OY2022 IFRO – 412 MW/0.1 Hz | Limit 1,240 MW
OY2023 IFRO – 463 MW/0.1 Hz | Limit 1,390 MW

## Slide 7: Hourly Average RRS Comparison

## Slide 8: Low Inertia Hours for FFR Prioritization NPRR 1128
If ERCOT comments dated July 15, 2022 on NPRR 1128 are approved,
  For certain selected hours FFR procurement up to FFR limit will be prioritized
ERCOT is considering a methodology that selects hours in the last two years wherein 25% of the time the system inertia in a 4-hour block is less than 185 GW∙s for FFR prioritization.
  The hours marked with a “1” in the table below represent hours for FFR prioritization.
Proposed
Notes: FFR priority hours.

## Slide 9: Comparison between ECRS and Non-Spin
ECRS and Non-Spin differ in the reliability risks these services address, qualification criteria, response time and duration. As a result, upon ECRS’ implementation, Non-Spin requirement cannot entirely be substituted by the amount of ECRS procured as was originally proposed during NPRR863 discussions.
 | ECRS | Non-Spin
Reliability Objective | ECRS may be deployed to Help restore the frequency to 60 Hz following a significant frequency deviation Provide energy upon detection of insufficient capacity for net load ramps Provide energy to avoid or during the implementation of an EEA Provide backup to Reg-Up | Non-Spin may be deployed to provide additional capacity, During situations when there isn’t sufficient capacity for energy dispatch For intra-day forced outage of units and during sustained frequency decay or sustained low frequency operations. When SCED does not have enough energy available to execute successfully
Primary Forecast Risk | Errors in intra-hour load/wind/solar forecast that is used in SCED | Errors in hourly load/wind/solar forecast that is used in RUC
Qualification Criteria | Provided using capacity that can be sustained at a specified level for two consecutive hours | Provided using capacity that can be sustained at a specified level for four consecutive hours
Response | Deployed within 10 minutes upon the receipt of deployment instruction | Deployed within 30 minutes upon the receipt of deployment instruction

## Slide 10: Non-Spinning Reserve Methodology - 2023
ERCOT is proposing the following changes in the methodology used to compute minimum Non-Spin requirements in 2023
  Before ECRS is implemented: Use 85th to 95th percentile of 10 HA max. net load forecast error
  After ECRS is implemented: Use 75th to 95th percentile of 6 HA hourly avg. net load forecast error
In 2023, ERCOT will continue the practice of monitoring the weather near Real Time and may procure up to an additional 1,000 MW of Non-Spin for specific Operating Hours.
The preliminary Non-Spin quantities for January 2023 through September 2023 in subsequent slides have been computed using current methodology (2020, 2021 and 2022 Net load and Net load Forecast), updated Wind Over-Forecast Error Adjustment table and the updated Solar Over-Forecast Error Adjustment table.
  Wind and Solar Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind and solar capacity, respectively.

## Slide 11: 2022 RUCs by Startup Time

## Slide 12: 2023 Intra-day Outage Table
The Intra-day Outage table helps account for increased capacity needs following forced outages of thermal resources within an operating day.

## Slide 13: Non-Spin Comparison May

## Slide 14: Non-Spin Comparison August

## Slide 15: Hourly Average Non-Spin Comparison

## Slide 16: ECRS Requirements Methodology - 2023
In 2023, ERCOT is proposing to compute ECRS requirements as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support net load forecast errors during sustained net load ramps.
Frequency Recovery Portion
  For various inertia levels, a medium-sized supply-side resource is tripped such that frequency nadir is just above 59.7 Hz. Amount of response needed equals to return frequency to 59.98 Hz is determined
  MWneed = (59.98 Hz – FreqB-point) * (1% load in MW/0.1 Hz)
  Calculated for each hour of each month from last two-year data
Intra-Hour Net Load Forecast errors (NLFE)
  85th – 95th percentile of 30-minute ahead intra-hour netload forecast errors for last two years
    The percentile is associated with the risk of net load ramp. The larger the netload ramp, the higher the percentile.
  An additional adjustment will be included to account for the impact of increase in the solar generation installed capacity on the net load forecast error.
The preliminary ECRS quantities for January 2023 through September 2023 in subsequent slides have been computed using the proposed methodology.

## Slide 17: Adjustment for Increase in Solar Installed Capacity
Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in 30-min ahead solar over forecast error per 1000 MW increase in installed solar capacity.
Additional ECRS per 1,000 MW increase in solar installed capacity
Adjustment for 2023 (Min: 0 MW | Mean: 74 MW | Max 283 MW)

## Slide 18: ECRS Requirement for 2023
 | Min | Mean | Max
ECRS | 1,209 MW | 1,981 MW | 3,039 MW
Frequency Recovery (F.R.)
Intra-Hour NLFE
w Solar Adjustment
 | Min | Mean | Max
F.R. | 574 MW | 974 MW | 1,572 MW
 | Min | Mean | Max
NLFE w Adj | 460 MW | 1008 MW | 2,027 MW
+

## Slide 19: Summary
In summary,
  ERCOT is not proposing any changes in the methodologies used to compute Regulation Service and RRS requirements for 2023.
  With the impending update in ERCOT’s 2023 IFRO, minimum RRS-PFR limit for 2023 will change to 1,390 MW.
  ERCOT is proposing some changes in the methodology used to compute minimum Non-Spin requirements in 2023. Specifically,
    Prior to ECRS: Use 85th to 95th percentile of 10 Hours Ahead (HA) max. net load forecast error
    After ECRS: Use 75th to 95th percentile of 6 HA hourly avg. net load forecast error
  Upon its implementation, ERCOT is proposing to compute ECRS requirements as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support sustained net load ramps.
ERCOT is requesting stakeholder feedback for changes to the 2023 A/S Methodology.

## Slide 20
Suggestions?

## Slide 21: 2023 Solar Adjustment Table Changes
2023 Methodology: There exists an upper bound on the amount of PVGR and wind ramp that are used in establishing GTBD. In 2023, in order to account for this upper bound, when computing the additional variability for which an adjustment is needed, the predicted PVGR and wind ramp calculation will partially discount the actual ramp from the previous 5-minutes.
2022 Methodology: When computing the additional variability for which an adjustment is needed, in 2022, the predicted PVGR and wind ramp calculation fully discounts the actual ramp from the previous 5-minutes.
Variability for which adjustment is needed.
Variability for which adjustment is needed.

## Slide 22: 2023 Solar Adjustment Tables
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity. The methodology for 2023 Solar Adjustment tables has been updated to better align it with how 5-minute wind and solar forecasted ramps are currently used in operations.
 | Min (MW) | Max (MW) | Average (MW)
Reg Up | 0 | 25.4 | 9.9
Reg Down | 0 | 22.4 | 8.2

## Slide 23: 2023 Wind Adjustment Tables
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind capacity.
Notes: Avg Reg Up adjustment for wind is 1.57 MW
Avg Reg Down adjustment for wind is 1.44 MW

## Slide 24: Regulation Comparison February

## Slide 25: Regulation Comparison March

## Slide 26: Regulation Comparison June

## Slide 27: 2022 Reg Up Exhaustion Rate and 2023 Quantities
In the first half of 2022, most Regulation Up exhaustion is in the evening hours around sunset.
Reg-Up
Hourly Average CPS1
2023 – 2022 Reg Up (%)

## Slide 28: 2023 Reg Down Exhaustion Rate and 2023 Quantities
In the first half of 2022, most Regulation Down exhaustion is in the morning hours around sunrise .
Reg-Down
Hourly Average CPS1
2023 – 2022 Reg Down (%)

## Slide 29: RRS-PFR from Energy Storage Resources (ESRs) in 2022
ESRs are providing larger volumes of RRS-PFR in 2022.
  ERCOT has modified its tools that measure performance of ESRs during Frequency Measurable Events (FMEs) beginning April 2022. Since then, ERCOT has been closely working with Resources that have not met the performance criteria.
*RRS-PFR from ESRs as a percentage of total RRS-PFR from CLRs, Gas, Coal and ESRs.
MW
Max: 878 MW
Avg: 269 MW
Percentage*
Max: 92%
Avg: 26%
Notes: Plot MWs I heat map format also

## Slide 30: 2023 RRS Table
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
*RRS Curr IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3088 | 3015 | 2982 | 2936 | 2898 | 2825 | 2732 | 2668
**RRS Upd IFRO (MW) | 3335 | 3287 | 3239 | 3195 | 3156 | 3079 | 3041 | 2991 | 2949 | 2871 | 2774 | 2705
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2618 | 2571 | 2538 | 2498 | 2450 | 2416 | 2375 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2651 | 2600 | 2562 | 2517 | 2466 | 2427 | 2381 | 2344 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,240 MW.
**RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,390 MW.
***Red font in table above identifies study scenario where RRS needed < 2300 MW. RRS requirement during these is based on the applicable floor.
****Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest
Notes: RRS quantity for 2022 decrease between 8 MW (310 GW.s case) and 82 MW (170 GW.s case)

## Slide 31: RRS Comparison February

## Slide 32: RRS Comparison March

## Slide 33: RRS Comparison July

## Slide 34: Low Inertia Hours for FFR Prioritization NPRR 1128
If ERCOT comments dated July 15, 2022 on NPRR 1128 are approved,
  For certain selected hours FFR procurement up to FFR limit will be prioritized
  ERCOT is considering a methodology that selects hours in the last 1 year wherein 75% of the time the system inertia is less than 200 GW∙s for FFR prioritization.
Notes: FFR priority hours.

## Slide 35: Adequacy of Non-Spin quantities in 2023
Between Jan 1, 2022 and Jul 31, 2022,
  ~5% of the time the available Non-Spin was not sufficient to cover the 6HA risk.
    Lowest Real Time headroom without RUC action was 2,366 MW on July 17@HE18. With RUC the Real Time headroom was around 3,488 MW.
  ~13% of the time the margin in the available Non-Spin to cover the 6HA risk was less than 1,430 MW.
Notes: Add ruc hours, remove ruc’ed capacity from headroom

## Slide 36: Non-Spin Comparison January

## Slide 37: Post ECRS Non-Spin Quantities
With the proposed “after ECRS approach” for Non-Spin, overall, the Non-Spin quantities are expected to decrease.
After ECRS Non-Spin
Min: 1,923 MW
Max: 4,112 MW
Pre-ECRS Non-Spin
Min: 2,669 MW
Max: 5,633 MW

## Slide 38: Net Load Variability Evaluation
Since July 12, 2021, ERCOT has been monitoring the weather forecast near Real Time and in during the following days has procured up to an additional 1,000 MW of Non-Spin during periods that were identified as having an increased potential of high forecast variability that may cause a higher net load during these hours.
  2021: Jul 29, Aug 1, Aug 2, Aug 14, Aug 27, Aug 29, Aug 30, Sep 3, Sep 4
  2022: Jan. 2, Jan. 3, Jan. 20, Feb. 3, Feb. 4, May 22, May 23, May 24, Jun 1
Additional Non-Spin may be procured for Operating Hours that are
  identified as having an increased potential of high forecast variability,
  there is a risk that the actual net load during these Operating Hours could be higher than forecast (after making appropriate forecast model selection) AND
  the expected available capacity and expected reserves including the posted minimum Non-Spin requirements during these Operating Hours is not sufficient to cover the projected net load forecast uncertainty risk.
In 2023, ERCOT is proposing to continue the practice of monitoring the weather near Real Time and may procure up to an additional 1,000 MW of Non-Spin for specific Operating Hours.

## Slide 39
August 18, 2022 | PDCWG
August 19, 2022 | WMWG
ERCOT Staff
Preliminary Methodology to Determine 2023 ECRS Requirements

## Slide 40: Introduction
ERCOT is in the process of implementing ERCOT Contingency Reserve Service (ECRS).
  ERCOT is targeting to implement ECRS prior to the “EMS freeze” period (around May 2023 – Jan 2024)
This presentation will discuss a proposed* methodology to determine the minimum quantities for ECRS in 2023. A spreadsheet that contains ECRS quantities from August 2022 through July 2023 that have been computed using this proposed methodology have been posted to today’s meeting page.
  ERCOT is seeking stakeholder feedback on the proposed ECRS methodology.
Note on Non-Spinning Reserve Service (Non-Spin) quantities post ECRS implementation
ECRS and Non-Spin differ in the reliability risks these services address, qualification criteria, response time and duration. As a result, upon ECRS’ implementation, Non-Spin requirement cannot entirely be substituted by the amount of ECRS procured as was originally proposed during NPRR863 discussions.
That said, ERCOT expects the risks that Non-Spin is used to cover will evolve upon ECRS’ implementation. Hence the methodology to determine Non-Spin quantities in a world where ECRS exists may need revisions.
  ERCOT plans to discuss the Non-Spin methodology that will apply with ECRS’ implementation as a part of the annual AS Methodology review process.
  * Note, ERCOT may refine the ECRS methodology further as a part of the annual effort to review the methodology for determining Ancillary Service (AS) quantities (AS Methodology).
Notes: WMWG | June 2022 ECRS Deployment Procedure (Part 1) | https://www.ercot.com/files/docs/2022/06/17/Preliminary_ECRS_Deployment_Procedure_v0_JuneWMWG.pptx
WMWG | July 2022 ECRS Deployment Procedure (Part 2) | https://www.ercot.com/files/docs/2022/07/26/Preliminary_ECRS_Deployment_Procedure_v0_JulyWMWG.pptx

## Slide 41: ECRS Requirements Methodology
ECRS is a service that is provided using capacity that can be sustained at a specified level for two consecutive hours and is used to restore or maintain the frequency of the ERCOT System:
  In response to significant depletion of RRS;
  As backup Regulation Service;
  By providing energy to avoid getting into or during an Energy Emergency Alert (EEA); and
  Upon detection of insufficient capacity for net load ramps.
ERCOT is proposing to compute ECRS requirements as the sum of,
  capacity needed to recover frequency following a large unit trip and
  capacity needed to support sustained net load ramps.
The next few slides will discuss the detail about each of these components that establish the ECRS requirements.

## Slide 42: Method for Determining MWs needed for Frequency Recovery
Capacity needed to recover frequency from B-point (i.e., settling frequency) to 59.98 Hz is determined by using dynamic simulations/studies that are run at varying inertia levels.
In every simulation, a single medium-size unit is tripped offline such that the C-point (frequency nadir) is stays just above 59.7 Hz*.
Capacity needed to recover frequency using this approach is determined for each hour of each month using two years historical data.
*59.7Hz is the trigger frequency for Load Resources that are providing RRS using an under-frequency relay.
  MWneed = (59.98 Hz – FreqB-point) * (1% load in MW/0.1 Hz)
B-point (settling frequency) is determined using dynamic simulations/studies that are run at varying inertia levels. In every simulation, a single medium-size unit is tripped offline such that the C-point (frequency nadir) is stays just above 59.7 Hz*.
60 Hz
59.7 Hz
B-point
59.98 Hz

## Slide 43: MWs needed for Frequency Recovery
 | Min | Mean | Max
MWneed | 574 MW | 951 MW | 1,572 MW

## Slide 44: Method for Determining Additional MWs needed for sustained Net Load Ramps
Capacity needed to support sustained net load ramps will be computed using
  85th to 95th percentile of 30-minute ahead intra-hour net load forecast errors for same hour same month of previous two years
    The percentile associated with every hour will be determined based on the risk of net load up ramp. Periods where the risk of net load ramp is highest will use 95th percentile and 85th percentile for periods with lowest risks.
  An additional adjustment will be included to account for the impact of increase in over-forecast error from expected growth in solar generation installed capacity.

## Slide 45: Regulation usage and SCED offset Trends
As the solar installed capacity has increased, during the evening hours, the magnitude of 10-min solar ramps have increased and there has been more reliance on regulation up deployments and SCED offsets.

## Slide 46: Projected Solar Generation Installed Capacity

## Slide 47: Adjustment for Increase in Solar Installed Capacity
Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in 30-min ahead solar over forecast error per 1000 MW increase in installed solar capacity.
Additional ECRS per 1,000 MW increase in solar installed capacity
Adjustment for 2023 (Min: 0 MW | Mean: 68 MW | Max 283 MW)

## Slide 48: MWs needed for Intra-hour Net Load Forecast Errors
 | Min | Mean | Max
MWneed | 403 MW | 913 MW | 1,889 MW
Without Solar Adjustment
With Solar Adjustment
 | Min | Mean | Max
MWneed | 403 MW | 981 MW | 2,027 MW

## Slide 49: ECRS Requirement for 2023
Total ECRS requirement for every hour is computed as the sum of
  capacity needed to recover frequency following a large unit trip and
  capacity needed to support sustained net load ramps (with solar adjustment)
 | Min | Mean | Max
ECRS | 1,093 MW | 1,933 MW | 3,039 MW

## Slide 50: Summary and Next Steps
Using the preliminary* methodology to determine the minimum quantities for ECRS, hourly ECRS requirements in 2023 may vary between 1,093 and 3,039 MW.
  A spreadsheet that contains the associated ECRS quantities for January through July of 2023 have been posted to today’s meeting page.
ERCOT is seeking stakeholder feedback on the proposed ECRS methodology.
Lastly, ERCOT expects the risks that Non-Spin is used to cover will evolve upon ECRS’ implementation. Hence the methodology to determine Non-Spin quantities in a world where ECRS exists may need revisions.
  ERCOT plans to discuss the Non-Spin methodology that will apply with ECRS’ implementation as a part of the annual AS Methodology review process.
* Note, ERCOT may refine the ECRS methodology further as a part of the annual effort to review the AS Methodology).

## Slide 51: ECRS May

## Slide 52: ECRS June

## Slide 53: Hourly Average ECRS