## Slide 1
ERCOT Frequency Control Report
September 2022
ERCOT
Operations Planning
PDCWG | Oct 28th, 2022

## Slide 2: Summary of September 2022
CPS1: 174.79%
Current CPS1 12-Month Rolling Average: 172.45%
0 BAAL Exceedance(s)
1 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2022 RMS1 Statistics
  Mean: 15.59 mHz
  Min: 12.43 mHz
  Max: 19.70 mHz
Energy Statistics
  Total Energy: 37,464,823 MWh
  Wind Energy: 5,755,040 MWh
  Percent Energy from Wind: 15.36 %
  Solar Energy: 2,516,064 MWh
  Percent Energy from Solar: 6.72%
Minimum System Inertia
  Mean: 260,395 MW*s
  Max: 302,440 MW*s on Sep 22th
  Min: 218,205 MW*s on Sep 30th
Notes: Data:
Mean: 260,395 MW*s
Max: 302,440 MW*s on Sep 22th
Min: 218,205 MW*s on Sep 30th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Sep-22 CPS1 (%): 174.79
Notes: 1. 52.81%@ 9/19/2022 HE 19:00
Expected Generation Deviation
Between 18:00-19:00 the Expected gen dev remained negative. The largest expected gen dev was -2290MW @ 6:20 PM with signification contribution from solar and wind generation.
IRR Ramps
Between 18:00-18:20 wind ramped down by ~250 MW
Between 18:00-19:00 solar ramped down by ~5235 MW
Steel load increase of approximately 360MW
A thermal unit had a ~200MW runback due to emission issues
Regulation: Regulation up was exhausted for most part of this hour. Multiple manual SCED offset of 100MW - 350 MW was applied.

## Slide 5: BAAL Exceedances & Violations
There is 0 BAAL exceedance(s) in September.

## Slide 6: 15-Minute Average CPS1%
Sep-22 CPS1 (%): 174.79
Notes: Overall the 15 min CPS1 score is above 160, Between 18:00 and 19:00 ,the CPS1 is between 130 to 150 due to solar down ramps.

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 172.45%
Notes: 12 month rolling average CPS1 score is 172.45, which is good and CPS1 score for Sep is slightly higher than the last month.

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year is so far slightly smaller overall compared with the 2021.
  Mean: 15.59 mHz
  Min: 12.43 mHz
  Max: 19.7 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by month
15.03Mhz on avg for Sep 2022

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Same data with 10 years shown instead of 15

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison
Notes: Comparison of frequency profile between Sep 2021 and Sep 2022, we see fewer instances of frequency hovering at or below the lower deadband in Sep 2022.

## Slide 13: Frequency Profile Comparison
Notes: Some story when you compare frequency profile between Sep 2021 and Sep 2022, we see fewer instances of frequency hovering at or below the lower deadband in Sep 2022.

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error
Notes: We did not make time error corrections and the time error was fairly small during the entire month of Sep.

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 37,464,823 MWh
There is an increase in total energy used in Sep compared to last year

## Slide 22: Total Energy from Wind Generation
Notes:   5,755,040 MWH
  We see a decrease in the wind energy production in September this year.

## Slide 23: % Energy from Wind Generation
Notes: 15.36%
of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 2,516,064 MWh
There is also a notable increase in solar energy production compared to August2022 and Sep 2021.

## Slide 25: % Energy from Solar Generation
Notes: 6.72% of total
energy was provided by solar generation, which is highest solar penetration level so far.

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia =201,953 MW*s on 09/30/2022
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 260,395 MW*s
Max: 302,440 MW*s on Sep 22th
Min: 218,205 MW*s on Sep 30th

## Slide 28: Questions?
Thank you!