## Slide 1
Nov 7, 2022
ROS
ERCOT Staff
Proposed 2023 Ancillary Service Methodology And Preliminary Quantities

## Slide 2: Stakeholder Discussion Timeline
September 14, 2022 – PDCWG (Methodology Discussion)
September 23, 2022 – WMWG (Methodology Discussion)
October 21, 2022 – WMWG (Proposed Methodology)
October 27, 2022 – OWG (Proposed Methodology)
October 28, 2022 – PDCWG (Proposed Methodology)
November 02, 2022 - WMS
November 07, 2022 - ROS
December 5, 2022 - TAC
December 20, 2022 – BoD

## Slide 3: Discussion Scope for Today
This presentation will discuss the proposed methodology for computing Ancillary Service (A/S) quantities in 2023.
  ERCOT is not proposing any changes in the methodologies used to compute Regulation Service and Responsive Reserve Service (RRS) requirements for 2023.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2023 assessment for ERCOT shows an increase in ERCOT’s IFRO. To align with ERCOT’s 2023 IFRO, minimum RRS-PFR limit for 2023 will change to 1,390 MW.
  ERCOT is proposing some changes in the methodology used to compute minimum Non-Spinning Reserve Service (Non-Spin) requirements in 2023. Specifically,
    Prior to ECRS: Use 85th to 95th percentile of 10 Hours Ahead (HA) max. net load forecast error
    After ECRS: Use 75th to 95th percentile of 6 HA hourly avg. net load forecast error
  Upon its implementation, ERCOT is proposing to compute ECRS requirements as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support sustained net load ramps.
The Ancillary Service (A/S) quantities for 2023 contained in this presentation are based on the methodology that was approved in December 2021.
  The quantities for 2023 reflect moving forward the historic data on which these are based, unless otherwise noted.
  Spreadsheets that contain the associated quantities and a redline version of the A/S Methodology document have been posted on today’s meeting page.

## Slide 4: Regulation Service Methodology
ERCOT is not proposing any change to the methodology used to compute the minimum Regulation Service requirements in 2023.
  The preliminary Regulation quantities for January 2023 through September 2023 have been computed using 2021 and 2022 five-minute net load variability, updated Wind Adjustment and Solar Adjustment tables*.
*Wind and Solar Adjustment tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind and solar capacity, respectively.

## Slide 5: Responsive Reserve Service (RRS) Methodology
ERCOT is not proposing any changes to methodology used to compute the minimum RRS requirements for 2023.
  The preliminary RRS quantities for January 2023 through September 2023 have been computed using 2021 and 2022 system inertia conditions and updated RRS table*.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2023 assessment for ERCOT shows an increase in ERCOT’s IFRO. To align with ERCOT’s 2023 IFRO, minimum RRS-PFR limit for 2023 will change to 1,390 MW.
*The RRS table tracks RRS requirements for different inertia conditions. This table was updated in 2023 to use a minimum RRS-PFR limit of 1,390 MW.
Notes: OY2022 IFRO – 412 MW/0.1 Hz | Limit 1,240 MW
OY2023 IFRO – 463 MW/0.1 Hz | Limit 1,390 MW

## Slide 6: NPRR 1128 | FFR Prioritization during Low Inertia Hours
If ERCOT comments dated July 15, 2022 on NPRR 1128 are approved and implemented, during certain selected hours when FFR is beneficial in improving reliability, FFR procurement up to FFR limit will be prioritized. In this regard,
  ERCOT is proposing to use a methodology that selects hours in the last two years wherein 25% of the time the system inertia in a 4-hour block is less than 185 GW∙s for FFR prioritization. The hours marked with a “1” in the table below represent hours for FFR prioritization.
Notes: FFR priority hours.

## Slide 7: Comparison between ECRS and Non-Spin
ECRS and Non-Spin differ in the reliability risks these services address, qualification criteria, response time and duration. As a result, upon ECRS’ implementation, Non-Spin requirement cannot entirely be substituted by the amount of ECRS procured as was originally proposed during NPRR863 discussions.
 | ECRS | Non-Spin
Reliability Objective | ECRS may be deployed to Help restore the frequency to 60 Hz following a significant frequency deviation Provide energy upon detection of insufficient capacity for net load ramps Provide energy to avoid or during the implementation of an EEA Provide backup to Reg-Up | Non-Spin may be deployed to provide additional capacity, During situations when there isn’t sufficient capacity for energy dispatch For intra-day forced outage of units and during sustained frequency decay or sustained low frequency operations. When SCED does not have enough energy available to execute successfully
Primary Forecast Risk | Errors in intra-hour load/wind/solar forecast that is used in SCED | Errors in hourly load/wind/solar forecast that is used in RUC
Qualification Criteria | Provided using capacity that can be sustained at a specified level for two consecutive hours | Provided using capacity that can be sustained at a specified level for four consecutive hours
Response | Deployed within 10 minutes upon the receipt of deployment instruction | Deployed within 30 minutes upon the receipt of deployment instruction

## Slide 8: Non-Spinning Reserve Methodology - 2023
ERCOT is proposing the following changes in the methodology used to compute minimum Non-Spin requirements in 2023,
  Before ECRS is implemented: Use 85th to 95th percentile of 10 HA max. net load forecast error
  After ECRS is implemented: Use 75th to 95th percentile of 6 HA hourly avg. net load forecast error
In 2023, ERCOT will continue the practice of monitoring the weather near Real Time and may procure up to an additional 1,000 MW of Non-Spin for specific Operating Hours.
The preliminary Non-Spin quantities for January 2023 through September 2023 in subsequent slides have been computed using 2020, 2021 and 2022 Net load and Net load Forecast, updated Wind and Solar Over-Forecast Error Adjustment tables and the updated Intra-day Outage table*.
*Wind and Solar Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed wind and solar capacity, respectively. The Intra-day Outage table accounts for increased capacity needs following forced outages of thermal resources within an operating day.

## Slide 9: 2022 RUCs by Startup Time

## Slide 10: Non-Spin Comparison May

## Slide 11: Non-Spin Comparison August

## Slide 12: Hourly Average Non-Spin Comparison

## Slide 13: ECRS Deployment/Release Conditions
ERCOT will deploy ECRS-Gen i.e. ECRS from SCED Dispatchable Resources when frequency drops below 59.91 Hz and available Reg-Up is not sufficient to restore frequency.
ERCOT may deploy ECRS-Gen under the following conditions,
  Trigger 1 : (PRC – 3200 MW) – (projected 10min Net Load ramp) + Remaining QSGR capacity < X MW
  Trigger 2: (10min ramp capacity) – (projected 10min Net Load ramp) < 0 MW
    ECRS will be deployed when there is lack of 10min ramping capacity.
Non-Controllable Load Resources that are providing ECRS will be separated into deployment groups as defined in Nodal Protocol Section 6.5.9.4.2 EEA Levels paragraph (2).
  Non-Controllable Load Resources that are providing ECRS can be deployed during an Emergency Condition either individually, in groups, or as an entire block providing Non-Spin. Deployments that do not encompass an entire block may be done to manage inertia, congestion, or for other local needs.
If a condition other than those listed above indicates that additional capacity may be needed to manage reliability, operators will evaluate the system condition and deploy ECRS as needed if no other better options are available to resolve the system condition. Under emergency, the emergency process will govern the deployment of ECRS.
As work on implementing ECRS in ERCOT systems progresses, ERCOT may further refine the procedure for ECRS deployment.
  Going forward, ERCOT plans to include a document that summarizes the procedure for ECRS deployment in the A/S Methodology posting.

## Slide 14: ECRS Requirements Methodology - 2023
In 2023, ERCOT is proposing to compute ECRS requirements as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support intra-hour net load forecast errors during sustained net load ramps.
Frequency Recovery Portion
  For various inertia levels, a medium-sized supply-side resource is tripped such that frequency nadir is just above 59.7 Hz. Amount of response needed equals to return frequency to 59.98 Hz is determined
  MWneed = (59.98 Hz – FreqB-point) * (1% load in MW/0.1 Hz)
  Calculated for each hour of each month from last two-year data
Intra-Hour Net Load Forecast errors (NLFE)
  85th – 95th percentile of 30-minute ahead intra-hour netload forecast errors for last two years
    The percentile is associated with the risk of net load ramp. The larger the netload ramp, the higher the percentile.
  An additional adjustment will be included to account for the impact of increase in the solar generation installed capacity on the net load forecast error.
The preliminary ECRS quantities for January 2023 through September 2023 in subsequent slides have been computed using the proposed methodology.

## Slide 15: ECRS Requirement for 2023
 | Min | Mean | Max
ECRS | 1,209 MW | 1,981 MW | 3,039 MW
Frequency Recovery (F.R.)
Intra-Hour NLFE
w Solar Adjustment
 | Min | Mean | Max
F.R. | 574 MW | 974 MW | 1,572 MW
 | Min | Mean | Max
NLFE w Adj | 460 MW | 1008 MW | 2,027 MW
+

## Slide 16: Summary
In summary,
  ERCOT is not proposing any changes in the methodologies used to compute Regulation Service and RRS requirements for 2023.
  To align with in ERCOT’s 2023 IFRO, minimum RRS-PFR limit for 2023 will change to 1,390 MW.
  ERCOT is proposing some changes in the methodology used to compute minimum Non-Spin requirements in 2023. Specifically,
    Prior to ECRS: Use 85th to 95th percentile of 10 Hours Ahead (HA) max. net load forecast error
    After ECRS: Use 75th to 95th percentile of 6 HA hourly avg. net load forecast error
  Upon its implementation, ERCOT is proposing to compute ECRS requirements as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support sustained net load ramps.
ERCOT is requesting ROS’ endorsement of the 2023 A/S Methodology.

## Slide 17
Suggestions?

## Slide 18: 2023 Solar Adjustment Tables
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity. The methodology for 2023 Solar Adjustment tables has been updated to better align it with how 5-minute wind and solar forecasted ramps are currently used in operations.
 | Min (MW) | Max (MW) | Average (MW)
Reg Up | 0 | 25.4 | 9.9
Reg Down | 0 | 22.4 | 8.2

## Slide 19: 2023 Wind Adjustment Tables
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind capacity.
Notes: Avg Reg Up adjustment for wind is 1.57 MW
Avg Reg Down adjustment for wind is 1.44 MW

## Slide 20: 2023 RRS Table
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
*RRS Curr IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3088 | 3015 | 2982 | 2936 | 2898 | 2825 | 2732 | 2668
**RRS Upd IFRO (MW) | 3335 | 3287 | 3239 | 3195 | 3156 | 3079 | 3041 | 2991 | 2949 | 2871 | 2774 | 2705
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2618 | 2571 | 2538 | 2498 | 2450 | 2416 | 2375 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2651 | 2600 | 2562 | 2517 | 2466 | 2427 | 2381 | 2344 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,240 MW.
**RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,390 MW.
***Red font in table above identifies study scenario where RRS needed < 2300 MW. RRS requirement during these is based on the applicable floor.
****Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest
Notes: RRS quantity for 2022 decrease between 8 MW (310 GW.s case) and 82 MW (170 GW.s case)

## Slide 21: 2023 Intra-day Outage Table
The Intra-day Outage table helps account for increased capacity needs following forced outages of thermal resources within an operating day.

## Slide 22: ECRS Adjustment for Increase in Solar Installed Capacity
Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in 30-min ahead solar over forecast error per 1000 MW increase in installed solar capacity.
Additional ECRS per 1,000 MW increase in solar installed capacity
Adjustment for 2023 (Min: 0 MW | Mean: 74 MW | Max 283 MW)

## Slide 23: ECRS Deployment/Release Conditions
ERCOT will deploy ECRS-Gen i.e. ECRS from SCED Dispatchable Resources when frequency drops below 59.91 Hz and available Reg-Up is not sufficient to restore frequency.
ERCOT may deploy ECRS-Gen under the following conditions,
  Trigger 1 : (PRC – 3200 MW) – (projected 10min Net Load ramp) + Remaining QSGR capacity < X MW
  Trigger 2: (10min ramp capacity) – (projected 10min Net Load ramp) < 0 MW
    ECRS will be deployed when there is lack of 10min ramping capacity.
Non-Controllable Load Resources that are providing ECRS will be separated into deployment groups as defined in Nodal Protocol Section 6.5.9.4.2 EEA Levels paragraph (2).
  Non-Controllable Load Resources that are providing ECRS can be deployed during an Emergency Condition either individually, in groups, or as an entire block providing Non-Spin. Deployments that do not encompass an entire block may be done to manage inertia, congestion, or for other local needs.
If a condition other than those listed above indicates that additional capacity may be needed to manage reliability, operators will evaluate the system condition and deploy ECRS as needed if no other better options are available to resolve the system condition. Under emergency, the emergency process will govern the deployment of ECRS.