## Slide 1: DWG Report to ROS
Zhenhua Wang – DWG Chair
November 7th, 2022

## Slide 2: DWG Update
DWG WebEx meeting on 10/18/2022
Future transitioning to REGC_C model
ROS approval of DWG procedure

## Slide 3
Future transitioning to REGC_C model
REGC_A model is 2nd generation (WECC) generic model used in PSSE software to represent renewable energy resources.
There are 521 renewable resources modeled in current DWG dynamic base cases. 244 use REGC_A (2022 DWG base case release).
REGC_C is a more advanced model developed by EPRI in partnership with WECC.

## Slide 4
REGC_A model vs REGC_C model:
  REGC_C model has approximate representation of inverter’s inner current control loop and phase lock loop
  REGC_C model can provide insight into inverter control instability that can be further studied in EMT domain
  REGC_C (and REGC_B) resolves numerical and convergence problems associated with REGC_A in low short circuit conditions
  REGC_C tested for consistent behavior across different software platforms including PSSE

## Slide 5
Timeline
  Current DWG case release is based on PSSE v33. Next release (2023) will be based on v35
  REGC_C is not included by PSSE v35 yet
  DWG will consider transition when REGC_C model is supported by PSSE v35
  REGC_C will require parameterization by OEMs