| RRGRR Number | 032 | RRGRR Title | Related to NPRR1132, Communicate Operating Limitations during Cold and Hot Weather Conditions |
| --- | --- | --- | --- |
| Date of Decision |  | June 2, 2022 |  |
| Action |  | Tabled |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined |  |
| Priority and Rank Assigned |  | To be determined |  |
| Resource Registration Glossary Sections Requiring Revision |  | Section 2 – Unit Information |  |
| Related Documents Requiring Revision/Related Revision Requests |  | Nodal Protocol Revision Request (NPRR) 1132, Communicate Operating Limitations during Cold and Hot Weather Conditions |  |
| Revision Description |  | This Resource Registration Glossary Revision Request (RRGRR) adds data required to be shared with the ERCOT as the Reliability Coordinator, Balancing Authority, and Transmission Operator for use in considering cold weather limitations in its Operational Planning Analysis, Real-Time monitoring, Real-Time assessments, and other analysis functions. ERCOT is also requiring this information for hot weather limitations. Finally, ERCOT is requiring Distributed Generation Resources (DGRs) and Distributed Energy Storage Resources (DESRs) to provide this information. ERCOT is also listing alternate fuel supply information to aid in the same analysis described above. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This RRGRR will add information required under North American Electric Reliability Corporation (NERC) Standards IRO-010-4 and TOP-003-5 for the Resource Entity to communicate the limits to be used for considering cold weather limitations. As a Reliability Coordinator, Balancing Authority, and Transmission Operator, ERCOT’s Data Specification identifies the data ERCOT uses for its Operational Planning Analysis, Real-Time monitoring, Real-Time assessments, and other analysis functions. While not required by NERC standards, ERCOT is also requiring Resource Entities to provide information regarding hot weather limitations. This RRGRR requires DGRs and DESRs to provide this information due to the increasing level of DGR and DESRs interconnecting to the ERCOT System. ERCOT is also listing required alternate fuel supply information to aid in the same analysis described above. This will help to more accurately reflect alternate fuel capabilities and limitations on units when in alternate fuel mode for support of Real-Time and look-ahead decision making. |  |
| ROS Decision |  | On 6/2/22, ROS voted unanimously to table RRGRR032 for further review by the Operations Working Group (OWG). All Market Segments participated in the vote. |  |
| Summary of ROS Discussion |  | On 6/2/22, participants requested OWG review RRGRR032. |  |

| Sponsor |  |
| --- | --- |
| Name | Nitika Mago / Stephen Solis |
| E-mail Address | Nitika.Mago@ercot.com / Stephen.Solis@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6601 / 512-248-6772 |
| Cell Number |  |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Brittney Albracht |
| E-Mail Address | Brittney.Albracht@ercot.com |
| Phone Number | 512-225-7027 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

None

Proposed Guide Language Revision

| SECTION 2: RESOURCE REGISTRATION GLOSSARY - Effective February 1, 2022 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Resource Registration Data |  | Wind |  | Solar Photovoltaic (PV) | [[RRGRR023 and RRGRR031: Insert applicable portions of column "Energy Storage System (ESS)" upon system implementation of NPRRs 1002, 1026, and 1029 for RRGRR023; or upon system implementation of NPRR995 for RRGRR031:] |  | Conventional Generation (Gen) |  | Combined Cycle (CC) |  | Load Resources |  | Distributed Generation | Notes |  | Field Name |  | Definition / Detailed Description | Screening Study (SS) (R, C, O, A) |  |  | Full Interconnect Study (FIS) - Steady-State, Short Circuit, and Facility (R, C, O, A) |  | FIS - Stability Study (R, C, O, A) |  | Planning Model (R, C, O, A) |  | Full Registration (R, C, O, A) |  |
| Unit Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information | X |  | X |  | X | X |  |  |  |  |  | X |  |  | Resource Site Code: |  | Enter the Site Code established in the General and Site Information tab of the GENERAL_SITE_ESIID_Information workbook. |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | All Caps | UNIT NAME |  | Enter Unit Code for the generator unit (e.g. Cedar Bayou Plant Gen 1 is "CBYG1"). |  |  | R | R |  | R |  | R |  | R |  |  |
| [RRGRR023 and RRGRR031: Replace applicable portions of "Unit Information - UNIT NAME" above with the following upon system implementation of NPRRs 1002, 1026, and 1029 for RRGRR023; or upon system implementation of NPRR995 for RRGRR031:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | All Caps | UNIT NAME |  | Enter Unit Code for the generator unit (e.g. Cedar Bayou Plant Gen 1 is "CBYG1"). For an ESS this is the name of the ESS while discharging. |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | Automatic | Resource Name (Unit Code/Mnemonic) |  | Concatenated mnemonic of Resource Site Code and Unit name (e.g. CBY_CBYG1). |  |  |  |  |  |  |  | A |  | A |  |  |
| [RRGRR023 and RRGRR031: Insert applicable portions of "Unit Information" rows below upon system implementation of NPRRs 1002, 1026, and 1029 for RRGRR023; or upon system implementation of NPRR995 for RRGRR031:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information |  |  |  |  | X |  |  |  |  |  |  |  |  | All Caps | Energy Storage System (ESS) Name |  | This name is used to tie ESS discharging and charging, prior to single ESS model era. |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information |  |  |  |  | X |  |  |  |  |  |  |  |  | All Caps | Dispatch Asset Code (provided by ERCOT) |  | For ESS enter the Dispatch Asset Code (this code will be provided by ERCOT). This code will be used for the ESS while charging. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information |  |  |  |  | X |  |  |  |  |  |  |  |  |  | ESIID assigned to meter |  | ESI ID number assigned to the meter. For NOIEs, the TDSP will create a non-settlement ESI ID. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information |  |  |  |  | X |  |  |  |  |  |  |  |  | Y/N | Wholesale Delivery Point? |  | Enter Y or N, if the point of delivery is a wholesale delivery point. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  |  |  |  |  |  |  | Y/N | Settlement Only Generator (SOG) |  | Refer to ERCOT Protocol Section 2.1, Definitions, for the definition of a Settlement Only Generator (SOG). |  |  |  |  |  |  |  | R |  | R |  |  |
| [RRGRR031: Replace "Unit Information - Settlement Only Generator (SOG)" above upon system implementation of NPRR995:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information | X |  | X |  | X | X |  |  |  |  |  |  |  | Y/N | Settlement Only Generator (SOG) or Settlement Only Energy Storage System (SOESS) |  | Refer to ERCOT Protocol Section 2.1, Definitions, for the definition of a Settlement Only Generator (SOG) and Settlement Only Energy Storage System (SOESS). |  |  |  |  |  |  |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  |  |  |  |  |  |  |  | PUC Registration Number |  | Enter the PUCT registration number. |  |  |  |  |  |  |  |  |  | O |  |  |
| [RRGRR023 and RRGRR029: Insert applicable portions of "Unit Information" rows below upon system implementation of NPRRs 1002, 1026, and 1029 for RRGRR023; or upon system implementation of NPRR1077 for RRGRR029:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information | X |  | X |  | X |  |  |  |  |  |  |  |  | Y/N | DC-Coupled Resource |  | Refer to ERCOT Protocol Section 2.1, Definitions, for the definition of a DC-Coupled Resource. |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information |  |  |  |  | X |  |  |  |  |  |  | X |  | Y/N | Self-Limiting Resource or Settlement Only Generator |  | Refer to ERCOT Protocol Section 2.1, Definitions, for the definition of a Self-Limiting Resource. |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | Y/N | Part of Self-Limiting Resource Facility |  | Refer to ERCOT Protocol Section 2.1, Definitions, for the definition of a Self-Limiting Resource Facility. |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | # | Self-Limiting Facility # |  | Self-Limiting Facility # 1, 2, 3….Leave blank if not Self-Limiting Facility. Refer to definition of Self-Limiting Facility in Protocol Section 2.1, Definitions. |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | Automatic | Site_Self-Limiting Facility# |  | Automatic field. All Resources that are part of the same Self-Limiting Facility will have same code. |  |  |  |  |  |  |  |  |  | A |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  |  | ERCOT Interconnection Project Number - Only New Units |  | Enter the ERCOT INR number. Required for new or upgraded units. |  |  |  | C |  | C |  | C |  | C |  |  |
| Unit Information | X |  | X |  | X | X |  |  |  |  |  |  |  |  | NERC Number |  | Enter NERC NCR number. |  |  |  |  |  |  |  |  |  | O |  |  |
| Unit Information | X |  | X |  | X | X |  |  |  |  |  |  |  | Y/N | Qualifying Facility |  | Refer to ERCOT Protocol Section 2 for the definition of Qualifying Facility. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | mm/dd/yyyy | Transmission Only MRD |  | Proposed model load date for RE-owned transmission equipment. |  |  |  |  |  |  |  |  |  | O |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | mm/dd/yyyy | Standard Generation Interconnection Agreement (SGIA) Signature Date |  | Enter the date the Resource signed SGIA. For NOIEs, use MOU date. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | mm/dd/yyyy | Unit Start Date (Model Ready Date) |  | Proposed model load date for unit. Required for new units only. |  |  |  |  |  |  |  |  |  | O |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | mm/dd/yyyy | Commercial Operations Date |  | Enter the unit's planned Commercial Operations Date. After the unit completes operational performance testing, this field should be updated by the RE with the actual Commercial Operations Date. |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | mm/dd/yyyy | Unit End Date |  | Entry of a date in this field will result in the unit being removed from the ERCOT model. Enter the model ready date of expected or actual retirement. Leave blank if not known/applicable. |  |  |  |  |  |  |  |  |  | O |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | All Caps | SubStation Code/SubStation Mnemonic |  | Enter the interconnecting transmission station code. If you need assistance in determining the corresponding ERCOT Substation Code\Mnemonic, please consult your TDSP, or ERCOT. For the SS/FIS, if a substation code cannot be identified, leave field blank and enter the expected electrical connection point as text in the comment section. |  |  | O | O |  | O |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | kV | Voltage Level |  | Enter the nominal voltage level at the Point of Interconnection Bus (e.g. 69kV, 138kV, 345kV). If you need assistance in determining the corresponding Voltage Level, please consult your TDSP, or ERCOT. |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | # | PTI Bus Number |  | Enter the PTI Bus Number at the Point of Interconnection Bus in the planning model. If you need assistance in determining the corresponding PTI Bus Number, please consult your TDSP, or ERCOT. |  |  | O | O |  | O |  | R |  | R |  |  |
| [RRGRR023 and RRGRR031: Insert applicable portions of "Unit Information - Transmission Station Load Name in Network Operations Model" below upon system implementation of NPRRs 1002, 1026, and 1029 for RRGRR023; or upon system implementation of NPRR995 for RRGRR031:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information |  |  |  |  | X |  |  |  |  |  |  |  |  | All Caps | Transmission Station Load Name in Network Operations Model |  | Enter the Load Name as listed in the ERCOT model as provided by the TDSP to be used by the ESS while charging. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | List | Primary Fuel Type |  | AB -- Agriculture Byproducts (bagasse, straw, energy crops) BFG -- Blast-Furnace Gas BIT -- Bituminous Coal BL -- Black liquor DFO -- Distillate Fuel Oil (diesel, No1 fuel oil, No 2 fuel oil, No 4 fuel oil) GEO -- Geothermal JF -- Jet Fuel KER -- Kerosene LFG -- Landfill Gas LIG -- Lignite MSW -- Municipal Solid Waste (refuse) NA -- Not Applicable NG -- Natural Gas (use this fuel type for steam turbines which are part of a Combined Cycle Train) NUC -- Nuclear (uranium, plutonium, thorium) OBG -- Other - Biomass Gas (methane, digester gas) OBL -- Other - Biomass Liquids (ethanol, fish oil, waste alcohol, other gases) OBS -- Other - Biomass Solids (animal manure/waster, medical waste, paper pellets, paper derived fuel) OG -- Other - Gas (butane, coal processes, coke-oven coal, methanol, refinery gas) OO -- Other - Oil (butane, crude, liquid byproducts, oil waste, propane) OTH -- Other (batteries, chemicals, hydrogen pitch sulfur, misc. technologies) PC -- Petroleum Coke PG -- Propane RFO -- Residual Fuel Oil (No 5 and No 6 fuel oil) STM -- Steam from other units SLW -- Sludge Waste SUB -- Sub-bituminous Coal SUN -- Solar (photovoltaic, thermal) TDF -- Tires T -- Tidal WAT -- Water (conventional, pumped storage) WDL -- Wood/Wood Waste - Liquids (red liquor, sludge wood spent sulfite liquor, other liquors) WDS -- Wood/Wood Waste - Solids (peat, railroad ties, utility poles, wood chips, other solids) WH -- Waste heat WND -- Wind WOC -- Waste / Other Coal |  |  | R | R |  | R |  | R |  | R |  |  |
| [RRGRR023: Replace "Unit Information - Primary Fuel Type" above with the following upon system implementation of NPRRs 1002, 1026, and 1029:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | List | Primary Fuel Type |  | AB -- Agriculture Byproducts (bagasse, straw, energy crops) BFG -- Blast-Furnace Gas BIT -- Bituminous Coal BL -- Black liquor DFO -- Distillate Fuel Oil (diesel, No1 fuel oil, No 2 fuel oil, No 4 fuel oil) GEO -- Geothermal JF -- Jet Fuel KER -- Kerosene LFG -- Landfill Gas LIG -- Lignite MSW -- Municipal Solid Waste (refuse) MWH -– Electricity (use this fuel type for battery energy storage) NA -- Not Applicable NG -- Natural Gas (use this fuel type for steam turbines which are part of a Combined Cycle Train) NUC -- Nuclear (uranium, plutonium, thorium) OBG -- Other - Biomass Gas (methane, digester gas) OBL -- Other - Biomass Liquids (ethanol, fish oil, waste alcohol, other gases) OBS -- Other - Biomass Solids (animal manure/waster, medical waste, paper pellets, paper derived fuel) OG -- Other - Gas (butane, coal processes, coke-oven coal, methanol, refinery gas) OO -- Other - Oil (butane, crude, liquid byproducts, oil waste, propane) OTH -- Other (chemicals, hydrogen pitch sulfur, misc. technologies) PC -- Petroleum Coke PG -- Propane RFO -- Residual Fuel Oil (No 5 and No 6 fuel oil) STM -- Steam from other units SLW -- Sludge Waste SUB -- Sub-bituminous Coal SUN -- Solar (photovoltaic, thermal) or DC-Coupled Resources combining photovoltaic and battery energy storage TDF -- Tires T -- Tidal WAT -- Water (conventional, pumped storage) WDL -- Wood/Wood Waste - Liquids (red liquor, sludge wood spent sulfite liquor, other liquors) WDS -- Wood/Wood Waste - Solids (peat, railroad ties, utility poles, wood chips, other solids) WH -- Waste heat WND -- Wind and DC-Coupled Resources combining wind and battery energy storage WOC -- Waste / Other Coal WND_SUN – DC-Coupled Resources combining wind, photovoltaic and battery energy storage |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | List | Secondary Fuel Type |  | Same data entry elements as primary fuel type, but for secondary or start-up fuel. |  |  | R | R |  | R |  | R |  | R |  |  |
| [RRGRR023: Replace "Unit Information - Secondary Fuel Type" above with the following upon system implementation of NPRRs 1002, 1026, and 1029:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | List | Secondary Fuel Type |  | Same data entry elements as primary fuel type, but for secondary or start-up fuel. For DC-Coupled Resource use MWH. |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  |  | X |  |  |  |  |  |  |  | List | Fuel Transportation Type |  | CV -- Conveyor PL -- Pipeline RR -- Railroad TK -- Truck NA -- Not Applicable |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  |  |  |  |  | X |  | List | Resource Category |  | Nuclear Hydro Coal and Lignite Combined Cycle ≤ 90 MW* Combined Cycle > 90 MW* Gas Steam - Supercritical Boiler Gas Steam - Reheat Boiler Gas Steam - Non-reheat or Boiler without air-preheater Simple Cycle ≤ 90 MW Simple Cycle > 90 MW Diesel Renewable Reciprocating Engine Solar Power Storage Other |  |  |  |  |  |  |  | R |  | R |  |  |
| [RRGRR023: Replace "Unit Information - Resource Category" above with the following upon system implementation of NPRRs 1002, 1026, and 1029:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information | X |  | X |  | X | X |  |  |  |  |  | X |  | List | Resource Category |  | Nuclear Hydro Coal and Lignite Combined Cycle ≤ 90 MW* Combined Cycle > 90 MW* Gas Steam - Supercritical Boiler Gas Steam - Reheat Boiler Gas Steam - Non-reheat or Boiler without air-preheater Simple Cycle ≤ 90 MW Simple Cycle > 90 MW Diesel Renewable Reciprocating Engine Solar Battery Energy Storage DC-Coupled Battery Energy Storage and Solar DC-Coupled Battery Energy Storage and Wind DC-Coupled Battery Energy Storage and Solar and Wind Other |  |  |  |  |  |  |  | R |  | R |  |  |
| Unit Information | X |  | X |  |  | X |  |  |  |  |  | X |  | Y/N | Renewable |  | Indicate if the unit is a Renewable Energy Credit (REC) generator, as certified with the PUCT. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information | X |  | X |  |  | X |  |  |  |  |  | X |  | Y/N | Renewable/Offset |  | REC offset generators that produce generation to cover offsets they have been approved to provide, as certified with the PUCT. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | List | Physical Unit Type |  | CA -- Combined cycle steam turbine part (includes steam part of integrated coal gasification combined cycle) CC -- Combined cycle total unit (use only for plants/generators that are in planning stage, for which specific generator details cannot be provided) CE -- Compressed air energy storage CS -- Combined cycle single shaft (combustion turbine and steam turbine share a single generator) CT -- Combined cycle combustion/gas turbine part (includes comb. turbine part of integrated coal gasification combined cycle) FC -- Fuel Cell GT -- Simple-cycle Combustion (gas) turbine (includes jet engine design) HY -- Hydraulic turbine (includes turbines associated with delivery of water by pipeline) IC -- Internal combustion (diesel, piston) engine NA -- Unknown at this time (planned units only) OT -- Other PS -- Hydraulic Turbine - Reversible (pumped storage) PV -- Photovoltaic ST -- Steam Turbine including nuclear, geothermal and solar. Does not include combined cycle. WT -- Wind Turbine |  |  | R | R |  | R |  | R |  | R |  |  |
| [RRGRR023: Replace "Unit Information - Physical Unit Type" above with the following upon system implementation of NPRRs 1002, 1026, and 1029:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | List | Physical Unit Type |  | BA -- Battery Energy Storage BA-PV -- DC-Coupled Battery Energy Storage and Photovoltaic BA-WT -- DC-Coupled Battery Energy Storage and Wind Turbine BA-PV-WT -- DC-Coupled Battery Energy Storage, Photovoltaic and Wind Turbine CA -- Combined cycle steam turbine part (includes steam part of integrated coal gasification combined cycle) CC -- Combined cycle total unit (use only for plants/generators that are in planning stage, for which specific generator details cannot be provided) CE -- Compressed air energy storage CS -- Combined cycle single shaft (combustion turbine and steam turbine share a single generator) CT -- Combined cycle combustion/gas turbine part (includes comb. turbine part of integrated coal gasification combined cycle) FC -- Fuel Cell GT -- Simple-cycle Combustion (gas) turbine (includes jet engine design) HY -- Hydraulic turbine (includes turbines associated with delivery of water by pipeline) IC -- Internal combustion (diesel, piston) engine NA -- Unknown at this time (planned units only) OT -- Other PS -- Hydraulic Turbine - Reversible (pumped storage) PV -- Photovoltaic ST -- Steam Turbine including nuclear, geothermal and solar. Does not include combined cycle. WT -- Wind Turbine |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | MVA | Name Plate Rating |  | Manufacturer designed MVA Rating of this unit at its rated power factor (gross). |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | MW | Real Power Rating |  | Manufacturer designed MW at rated power factor (gross). |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | MVAR | Reactive Power Rating |  | Manufacturer designed MVAr at rated power factor (gross). |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  |  | X |  | X |  |  |  |  |  | MW | Turbine Rating |  | Manufacturer designed MW of the turbine (gross). |  |  | C | C |  | C |  | R |  | C |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | kV | Unit Generating Voltage |  | Terminal voltage of generating unit, as modeled (typically equivalent to low side of GSU). |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  |  | Governor Droop Setting |  | The percent change in frequency that will cause generator output to change from no Load to full Load. (e.g. for 5%, use .05). |  |  |  |  |  |  |  |  |  | C |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | Hz | Governor Dead-band |  | The range of deviations of system frequency (+/-) that produces no Primary Frequency Response. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | degree F | Design Maximum Ambient Temperature |  | This is the maximum (high) ambient dry bulb temperature at which the unit is designed to operate. This field must be completed if the design temperature is known. |  |  |  |  |  |  |  |  |  | C |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | degree F | Design Minimum Ambient Temperature |  | This is the minimum (low) ambient dry bulb temperature at which the unit is designed to operate. This filed must be completed if the design temperature is known. |  |  |  |  |  |  |  |  |  | C |  |  |
| Unit Information |  |  |  |  |  | X |  | X |  |  |  | X |  | degree F | Maximum Historical Operating Temperature |  | The highest ambient dry bulb temperature at which the unit has operated without a Forced Outage, Startup Loading Failure, or Forced Derate due to hot weather. If the unit has not operated through a complete summer Peak Load Season, the design maximum or engineering analysis maximum should be used in place of an actual historical operating temperature. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information |  |  |  |  |  | X |  | X |  |  |  | X |  | degree F | Minimum Historical Operating Temperature |  | The lowest ambient dry bulb temperature at which the unit has operated without a Forced outage, Startup Loading Failure, or Forced Derate due to cold weather. If the unit has not operated through a complete winter Peak Load Season, the design minimum or engineering analysis minimum should be used in place of an actual historical operating temperature. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | degree F | Engineering Analysis Maximum Ambient Temperature |  | The highest ambient dry bulb temperature at which the Resource can operate as determined by an engineering analysis. The engineering analysis shall be performed at least once every five years and this value shall be updated as necessary after each engineering analysis. |  |  |  |  |  |  |  |  |  | C |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  | X |  | degree F | Engineering Analysis Minimum Ambient Temperature |  | The lowest ambient dry bulb temperature determined at which the Resource can operate as determined by an engineering analysis. The engineering analysis shall be performed at least once every five years and this value shall be updated as necessary after each engineering analysis. |  |  |  |  |  |  |  |  |  | C |  |  |
| Unit Information |  |  |  |  |  | X |  | X |  |  |  | X |  | Hours at maximum output | Alternate Fuel Supply Availability |  | Winter season alternate fuel minimum supply inventory level. |  |  |  |  |  |  |  |  |  | R |  |  |
| Unit Information |  |  |  |  |  | X |  | X |  |  |  | X |  | MW | Real Power Maximum Rating on Alternate Fuel |  | Operational maximum MW at rated power (gross) using Alternate Fuel |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information |  |  |  |  |  | X |  | X |  |  |  | X |  | MW | Real Power Minimum Rating on Alternate Fuel |  | Minimum sustainable operating MW at rated power (gross) using Alternate Fuel |  |  | R | R |  | R |  | R |  | R |  |  |
| Unit Information |  |  |  |  |  | X |  | X |  |  |  | X |  | Hours | Time to Switch to Alternate Fuel |  | Time required to transition from being On-Line with primary fuel to alternate fuel Real Power Minimum Rating on Alternate Fuel. This includes time to bring unit offline, if needed. |  |  | R | R |  | R |  | R |  | R |  |  |
| [RRGRR019 and RRGRR023: Insert applicable portions of "Unit Information - Switchable Generation Resource" below upon system implementation of RRGRR019 or NPRRs 1002, 1026, and 1029 respectively:] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit Information | X |  | X |  | X | X |  | X |  |  |  |  |  | Y/N | Switchable Generation Resource |  | Is the unit able to switch between the ERCOT Control Area and a non-ERCOT Control Area? |  |  | R | R |  | R |  | R |  | R |  |  |