## Slide 1
PDCWG Report to ROS
Chair: Jimmy Jackson, CPS
Vice Chair: Chad Mulholland, NRG
ROS
Nov 7th, 2022

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs and IMFR
    1 FME in the month of Sep
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 10/28/2022
  Review of 2023 A/S Methodology
  NPRR1143 Discussion
  Addition of Inertia data to the ROS report Discussion
  ERCOT Reports
  TRE Report

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 1 FME in September
  9/5/2022 23:48:10
    Loss of 1208 MW of generation
    Interconnection Frequency Response: 1610 MW/0.1 Hz
    91 Resources were evaluated. These includes,
      38 Generation Resources
      1 Controllable Load Resource
      52 Energy Storage Resources
    6 of 91 Evaluated Resources had less than 75% of their expected Initial Primary Frequency Response.
    5 of 91 Evaluated Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 412 MW/0.1 Hz
IMFR Performance currently
1210.77 MW/0.1HZ

## Slide 7
Questions?

## Slide 8: Frequency Control Report
Sep 2022

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency
Notes: 15.03Mhz on avg for Sep 2022

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections

## Slide 13: ERCOT Total Energy
Notes: 37,464,823 MWh

## Slide 14: ERCOT Total Energy from Wind Generation
Notes:   5,755,040 MWh

## Slide 15: ERCOT % Energy from Wind Generation
Notes: 15.36%

## Slide 16: ERCOT Total Energy from Solar Generation
Notes: 2,516,064 MWh

## Slide 17: ERCOT % Energy from Solar Generation
Notes: 6.72%

## Slide 18: ERCOT Daily Minimum System Inertia
Notes: Previous Minimum was 109,029 MW*s on 3/22/2021
Sep Data:
Mean: 260,395 MW*s
Max: 302,440 MW*s on Sep 22th
Min: 218,205 MW*s on Sep 30th

## Slide 19: ERCOT Inertia Trend
Date and Time | 2013 3/10 3:00 AM | 2014 3/30 3:00 AM | 2015 11/25 2:00 AM | 2016 4/10 2:00 AM | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021 03/22 00:00 AM | 2022 03/21 01:00 AM
Min synch. Inertia (GW*s) | 132 | 135 | 152 | 143 | 130 | 128.8 | 134.5 | 131.1 | 109 | 115
System load at minimum synch. Inertia (MW) | 24,726 | 24,540 | 27,190 | 27,831 | 28,425 | 28,397 | 29,883 | 30,679 | 32,599 | 33,365
Non-synch. Gen. in % of System Load | 31 | 34 | 42 | 47 | 54 | 53 | 50 | 57 | 65 | 66
Notes: For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.