| NPRR Number | 1138 | NPRR Title | Communication of Capability and Status of Online IRRs at 0 MW Output |
| --- | --- | --- | --- |
| Date of Decision |  | June 9, 2022 |  |
| Action |  | Tabled |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined |  |
| Priority and Rank Assigned |  | To be determined |  |
| Nodal Protocol Sections Requiring Revision |  | 3.15.3, Generation Resource Requirements Related to Voltage Support 6.5.5.1, Changes in Resource Status |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) requires each Resource Entity to ensure that the reactive capability curve submitted for any Intermittent Renewable Resource (IRR) accurately reflects the IRR’s reactive capability when it is not providing real power and at lower levels of real power output. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | This NPRR introduces requirements to improve consistency in the reporting of reactive capabilities of IRRs. ERCOT has observed a variety of practices to represent reactive capabilities at low levels of output and at no real power output. For example, Resource Entities for some IRRs have reported no reactive capability below 10% of the IRR’s nameplate capacity. While those IRRs may not be required to have reactive capability at that level of real power output, IRRs will generally have some capability below that level, and ERCOT still needs to have an accurate understanding of that capability for its operations and planning purposes. ERCOT also has a particular need to know the amount of Reactive Power capability the IRR has when it is producing no real power. If a unit is able to produce Reactive Power when it is not producing real power and the unit remains synchronized to the ERCOT System, this Reactive Power capability must be coordinated with other voltage control actions of the Transmission Service Provider (TSP) for real time voltage control in Real-Time Operations. If a unit is not able to produce Reactive Power when it is not producing real power, ERCOT should be aware of that fact so that it does not mistakenly depend on the IRR for Reactive Power in such circumstances. If an IRR cannot provide Reactive Power when it is not producing real power, and the IRR is contributing to a voltage or stability issue, the IRR may be disconnected consistent with paragraph (4)(e) of Section 3.15, Voltage Support. This NPRR requires each Resource Entity to ensure that each of its IRRs’ reactive capability curves accurately reflects the IRR’s reactive capability at this lowest output level. This NPRR also standardizes IRR practices with respect to setting Low Sustained Limit (LSL) values and providing telemetry of Automatic Voltage Regulator (AVR) statuses when an IRR is at zero real power output. Some IRRs have demonstrated oscillations with unstable Reactive Power control at very low MW output levels due to equipment limitations, necessitating that the LSL be set at a slightly higher level that avoids these oscillations. However, in some cases, these LSL values are set too high. Resource Entities representing IRRs must ensure these equipment limitations are minimized to allow the LSL to be set as close to 0 MW as possible, including coordinating with the Original Equipment Manufacturer if necessary. The standardization of these practices will help ensure that ERCOT studies accurately identify voltage and stability issues and will provide greater clarity of ERCOT’s expectations for IRRs in the interconnection process. ERCOT notes that, while this NPRR does not modify reactive capability requirements for IRRs, it is requiring that whatever reactive capability an IRR has must be utilized to maintain voltage at the IRR’s Point of Interconnection Bus (POIB) even if the IRR has no real power output. |  |
| Credit Work Group Review |  | To be determined |  |
| PRS Decision |  | On 6/9/22, PRS voted unanimously to table NPRR1138 and refer the issue to WMS and ROS. All Market Segments participated in the vote. |  |
| Summary of PRS Discussion |  | On 6/9/22, participants requested that PRS table and refer NPRR1138 to WMS and ROS for further discussions regarding NPRR1138’s proposed requirements. |  |

| Sponsor |  |
| --- | --- |
| Name | Stephen Solis |
| E-mail Address | Stephen.solis@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6772 |
| Cell Number | 512-426-4721 |
| Market Segment | Not Applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Jordan Troublefield |
| E-Mail Address | Jordan.Troublefield@ercot.com |
| Phone Number | 512-248-6521 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None |  |

Market Rules Notes

Please note that the following NPRR(s) also propose revisions to the following section(s):

- NPRR1085, Ensuring Continuous Validity of Physical Responsive Capability (PRC) and Dispatch through Timely Changes to Resource Telemetry and Current Operating Plans (COPs)

  - Section 6.5.5.1

- NPRR1100, Allow Generation Resources and Energy Storage Resources to Serve Customer Load When the Customer and the Resource are Disconnected from the ERCOT System

  - Section 6.5.5.1

Proposed Protocol Language Revision

- 3.15.3	Generation Resource Requirements Related to Voltage Support

(1)	Generation Resources required to provide VSS shall have and maintain Reactive Power capability at least equal to the Reactive Power capability requirements specified in these Protocols and the ERCOT Operating Guides.

(2)	Generation Resources providing VSS shall be compliant with the ERCOT Operating Guides for response to transient voltage disturbance.

(3)	Generation Resources providing VSS must meet technical requirements specified in Section 8.1.1.1, Ancillary Service Qualification and Testing, and the performance standards specified in Section 8.1.1, QSE Ancillary Service Performance Standards.

(4)	Each Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the automatic voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is telemetering its Resource Status as STARTUP, SHUTDOWN, or ONTEST, or the QSE determines a need to operate in manual mode due to an undue threat to safety, undue risk of bodily harm, or undue damage to equipment at the generating plant.

(5)	Each Generation Resource providing VSS shall maintain the Voltage Set Point established by ERCOT, the interconnecting TSP, or the TSP’s agent, subject to the Generation Resource’s operating characteristic limits, voltage limits, and within tolerances identified in paragraph (4) of Nodal Operating Guide Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource Requirements.

(6)	The reactive capability required must be maintained at all times that the Generation Resource is On-Line.

(7)	Each QSE shall send to ERCOT, via telemetry, the AVR and Power System Stabilizer (PSS) status for each of its Generation Resources providing VSS.  For AVRs, an “On” status will indicate the AVR is on and set to regulate the Resource’s terminal voltage in the voltage control mode, and an “Off” status will indicate the AVR is off or in a manual mode.  For PSS, an “On” status will indicate the service is enabled and ready for service, and an “Off” status will indicate it is off or out of service.  Each QSE shall monitor the status of its Generation Resources’ regulators and stabilizers, and shall report status changes to ERCOT.

(8)	Each Resource Entity shall provide information related to the tuning parameters, local or inter-area, of any PSS installed at a Generation Resource.

(9)	For each IRR that is not equipped with the capability to provide Reactive Power when it is not producing real power, each Resource Entity shall:

(a)	Ensure its Low Sustained Limit (LSL) is set at the lowest MW level, not to exceed 1 MW, at which the IRR can provide stable Reactive Power output, after appropriate tuning of settings;

(b)	Ensure its lowest MW point on its submitted reactive capability curve reflects 0 MVAr leading and lagging reactive capability at 0 MW;

(c)	Ensure its second-lowest MW point on its submitted reactive capability curve is set to accurately reflect its leading and lagging reactive capability at its LSL; and

(d)	Send to ERCOT, via telemetry, an AVR status of “On” when it is synchronized to the ERCOT System and not producing real power.

(10)	For each IRR that is equipped with the capability to provide Reactive Power when it is not producing real power, each Resource Entity shall:

(a)	Ensure it can provide stable Reactive Power output at all MW levels at which the IRR has Reactive Power capability;

(b)	Set its LSL to 0 MW;

(c)	Ensure its lowest MW point on its submitted reactive capability curve accurately reflects its MVAr leading and lagging reactive capability when it is not producing real power;

(d)	Send to ERCOT, via telemetry, an AVR status of “On” when it is synchronized to the ERCOT System and not producing real power; and

(e)	Meet the requirements identified in paragraphs (2), (4), (5), and (7) above when it is synchronized to the ERCOT System and not producing real power.

[NPRR989 and NPRR1026: Replace applicable portions of Section 3.15.3 above with the following upon system implementation:] - 3.15.3 Generation Resource and Energy Storage Resource Requirements Related to Voltage Support (1) Generation Resources and ESRs required to provide VSS shall have and maintain Reactive Power capability at least equal to the Reactive Power capability requirements specified in these Protocols and the ERCOT Operating Guides. (2) Generation Resources and ESRs providing VSS shall be compliant with the ERCOT Operating Guides for response to transient voltage disturbance. (3) Generation Resources and ESRs providing VSS must meet technical requirements specified in Section 8.1.1.1, Ancillary Service Qualification and Testing, and the performance standards specified in Section 8.1.1, QSE Ancillary Service Performance Standards. (4) Each Generation Resource and ESR providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the automatic voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is telemetering its Resource Status as STARTUP, SHUTDOWN, or ONTEST, or the QSE determines a need to operate in manual mode due to an undue threat to safety, undue risk of bodily harm, or undue damage to equipment at the generating plant. (5) Each Generation Resource and ESR providing VSS shall maintain the Voltage Set Point established by ERCOT, the interconnecting TSP, or the TSP’s agent, subject to the Generation Resource’s or ESR’s operating characteristic limits, voltage limits, and within tolerances identified in paragraph (4) of Nodal Operating Guide Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource Requirements. (6) The reactive capability required must be maintained at all times that the Generation Resource or ESR is On-Line. (7) Each QSE shall send to ERCOT, via telemetry, the AVR and Power System Stabilizer (PSS) status for each of its Generation Resources providing VSS. Each QSE shall send to ERCOT via telemetry the AVR status for each of its ESRs providing VSS. For AVRs, an “On” status will indicate the AVR is on and set to regulate the Resource’s terminal voltage in the voltage control mode, and an “Off” status will indicate the AVR is off or in a manual mode. For PSS, an “On” status will indicate the service is enabled and ready for service, and an “Off” status will indicate it is off or out of service. Each QSE shall monitor the status of its Generation Resources’ and ESRs’ regulators and stabilizers, and shall report status changes to ERCOT. (8) Each Resource Entity shall provide information related to the tuning parameters, local or inter-area, of any PSS installed at a Generation Resource. (9) If any individual Resource within a Self-Limiting Facility is incapable of meeting its Reactive Power requirement at the POI, the QSE must bring On-Line additional Resource(s) within the Self-Limiting Facility to provide VSS as specified in paragraph (4) of Section 3.15, Voltage Support, while respecting the limit on MW Injection. (10) For each IRR that is not equipped with the capability to provide Reactive Power when it is not producing real power, each Resource Entity shall: (a) Ensure its Low Sustained Limit (LSL) is set at the lowest MW level, not to exceed 1 MW, at which the IRR can provide stable Reactive Power output, after appropriate tuning of settings; (b) Ensure its lowest MW point on its submitted reactive capability curve reflects 0 MVAr capability leading and lagging at 0 MW; (c) Ensure its second lowest MW point on its submitted reactive capability curve is set to accurately reflect its leading and lagging reactive capability at its LSL; and (d) Send to ERCOT, via telemetry, an AVR status of “On” when it is synchronized to the ERCOT System and not producing real power. (11) For each IRR that is equipped with the capability to provide Reactive Power when it is not producing real power, each Resource Entity shall: (a) Ensure it can provide stable Reactive Power output at all MW levels and set its LSL to 0 MW; (b) Ensure its lowest MW point on its submitted reactive capability curve accurately reflects its MVAr leading and lagging reactive capability when it is not producing real power; (c) Send to ERCOT, via telemetry, an AVR status of “On” when it is synchronized to the ERCOT System and not producing real power; and (d) Meet the requirements identified in paragraphs (2), (4), (5), and (7) above.

6.5.5.1	Changes in Resource Status

(1)	Each QSE shall notify ERCOT of a change in Resource Status via telemetry and through changes in the Current Operating Plan (COP) as soon as practicable following the change.

(2)	Each QSE shall promptly inform ERCOT when the operating mode of its Generation Resource’s Automatic Voltage Regulator (AVR) or Power System Stabilizer (PSS) is changed while the Resource is On-Line.  The QSE shall also provide the Resource’s AVR or PSS status logs to ERCOT upon request.

(3)	Each QSE shall immediately report to ERCOT and the TSP any inability of the QSE’s Generation Resource required to meet its reactive capability requirements in these Protocols.

(4)	Each Resource Entity and QSE shall, for each Intermittent Renewable Resource (IRR) that is not capable of providing real power due to a lack of a renewable fuel source and that remains synchronized to the ERCOT System, send to ERCOT, via telemetry, a Real-Time On-Line status and an HSL and LSL of 0.