## Slide 1
ERCOT Frequency Control Report
October 2022
ERCOT
Operations Planning
PDCWG | November 16th, 2022

## Slide 2: Summary of September 2022
CPS1: 174.70%
Current CPS1 12-Month Rolling Average: 172.76%
0 BAAL Exceedance(s)
0 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2020
2020 BAAL-003 FRM Performance: -789.34
2022 RMS1 Statistics
  Mean: 15.53 mHz
  Min: 12.43 mHz
  Max: 19.70 mHz
Energy Statistics
  Total Energy: 32,239,191 MWh
  Wind Energy: 7,377,412 MWh
  Percent Energy from Wind: 22.88%
  Solar Energy: 2,031,912 MWh
  Percent Energy from Solar: 6.30%
Minimum System Inertia
  Mean: 190,225 MW*s
  Max: 244,459 MW*s on Oct 13th
  Min: 123,509 MW*s on Oct 22nd
Notes: Data:
Mean: 260,395 MW*s
Max: 302,440 MW*s on Sep 22th
Min: 218,205 MW*s on Sep 30th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Oct-22 CPS1 (%): 174.70

## Slide 5: BAAL Exceedances & Violations
There is 0 BAAL exceedance(s) in October.

## Slide 6: 15-Minute Average CPS1%
Oct-22 CPS1 (%): 174.70
Notes: Overall the 15 min CPS1 score is above 160, Between 18:00 and 19:00 ,the CPS1 is between 130 to 150 due to solar down ramps.

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 172.76%
Notes: 12 month rolling average CPS1 score is 172.45, which is good and CPS1 score for Sep is slightly higher than the last month.

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year is so far slightly smaller overall compared with the 2021.
  Mean: 15.53 mHz
  Min: 12.43 mHz
  Max: 19.7 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by month
15.03Mhz on avg for Oct 2022

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Same data with 10 years shown instead of 15

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison
Notes: Comparison of frequency profile between Sep 2021 and Sep 2022, we see fewer instances of frequency hovering at or below the lower deadband in Sep 2022.

## Slide 13: Frequency Profile Comparison
Notes: Some story when you compare frequency profile between Sep 2021 and Sep 2022, we see fewer instances of frequency hovering at or below the lower deadband in Sep 2022.

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error
Notes: We did not make time error corrections and the time error was fairly small during the entire month of Sep.

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2020 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2020 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO =

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 32,239,191 MWh

## Slide 22: Total Energy from Wind Generation
Notes:   7,377,412 MWH

## Slide 23: % Energy from Wind Generation
Notes: 22.88%
of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 2,031,912 MWh

## Slide 25: % Energy from Solar Generation
Notes: 6.30 %of total
energy was provided by solar generation, which is highest solar penetration level so far.

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia =123,509 MW*s on 10/22/2022
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 190,225 MW*s
Max: 244,459 MW*s on Oct 13th
Min: 123,509 MW*s on Oct 22nd

## Slide 28: ERCOT Inertia 2013-2022(Jan-Oct)
Date and Time | 2013 3/10 3:00 AM | 2014 3/30 3:00 AM | 2015 11/25 2:00 AM | 2016 4/10 2:00 AM | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021 03/22 00:00 AM | 2022 03/21 01:00 AM
Min synch. Inertia (GW*s) | 132 | 135 | 152 | 143 | 130 | 128.8 | 134.5 | 131.1 | 109 | 115
System load at minimum synch. Inertia (MW) | 24,726 | 24,540 | 27,190 | 27,831 | 28,425 | 28,397 | 29,883 | 30,679 | 32,599 | 33,365
Non-synch. Gen. in % of System Load | 31 | 34 | 42 | 47 | 54 | 53 | 50 | 57 | 65 | 66
Notes: For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.

## Slide 29: Questions?
Thank you!