## Slide 1
Regulation Bias Analysis Post SCR-773
October 2022
ERCOT
Operations Planning
PDCWG | November 14th, 2022

## Slide 2
Discussion Points
Current GTBD Parameters & References
Metric to measure Regulation bias and performance
Regulation Deployed comparison for last three months.
Total Regulation (net) Deployed Comparison
Regulation Deployed 15-minute interval comparison by each hour for 2020, 2021, and 2022 months
Regulation Exhaustion Rate
Regulation bias for consecutive 5-min SCED intervals
Time Error & Contributing Factors
Summary

## Slide 3: Current GTBD Parameters
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 – K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 – 10:05 AM – K6 Changed from 0 to 0.5
2/12/19 – 2:15 PM – K6 changed from 0.5 to 1.0
3/12/19 – 2:10 PM – PWRR Threshold from 10 to 15 MW/min
3/19/19 – 2:15 PM – PWRR Threshold from 15 to 20 MW/min
4/01/19 – 10:00 AM – K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 – 1:15 PM – Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – 1:10 PM – K5 changed from 0.4 to 0.5, Max Integral ACE feedback changed from 160 to 200, PWRR Threshold changed from 25 to 30
6/17/20 – 10 AM - PWRR Calculation method changed from Direct to Interpolated
9/1/20 – 11 AM - Max Integral ACE Feedback changed from 200 to 250
9/3/20 – 3 PM - Max Integral ACE Feedback changed from 250 to 300
9/4/20 – 3 PM - Max Integral ACE Feedback changed from 300 to 250
6/1/21 – 10:00 AM – K8 Changed from 0 to 0.5, PSRR Threshold changed to 10
6/2/21 – 10:00 AM – PSRR Threshold changed from 10 to 20
6/3/21 – 10:00 AM – K8 Changed from 0.5 to 0.75
6/4/21 – 10:00 AM – K8 Changed from 0.75 to 1
9/2/21 – 10:00 AM – PSRR Threshold changed to 30
6/7/22 – 10:30 AM – K7 Changed from 0 to 0.5, PDCTRR Min/Max Threshold changed to 10 MW/min
6/8/22 – 10:30 AM – PDCTRR Min/Max Threshold changed from 10 to 20 MW/min
6/9/22 – 10:30 AM – K7 Changed from 0.5 to 0.75
6/10/22 – 10:30 AM – K7 Changed from 0.07 to 1.0
7/21/22 – 10:00 AM–Max Integral ACE Feedback changed from 250 to 350
7/21/22 – 05:10 PM – K5 Changed from 0.5 to 1
7/22/22 – 09:40 PM – K5 Changed from 1 to 0.5
7/27/22 – 08:40 AM – PSRR Threshold changed to 40 MW/min

## Slide 4: Projected Wind Ramp Rate MAE
Notes: For intra-hour wind ramp forecast, SCED PWRR MAE is fairly consistent and smaller than the persistence forecast across the board.

## Slide 5: Projected Wind Ramp Rate Error
Notes: PWRR error is higher during the ramp up and ramp down hours. Regardless of the ramping magnitude, SCED PWRR is consistent and performing significantly better than the persistence forecast

## Slide 6: Projected Solar Ramp Rate MAE
Notes: For intra-hour solar ramp forecast, SCED PSRR is performing significantly better especially during the solar up ramp and down ramp hours compared to the persistence forecast

## Slide 7: Projected Solar Ramp Rate Error
Notes: Similar to wind, generally we see bigger forecast errors during ramping periods.

## Slide 8: References

## Slide 9
Metrics to Measure SCR-773 Performance
Trend and monitor the regulation deployed by hour.
Set target of 50 MW for total regulation deployed by hour for peak hours.
Set target of 85% for the number of intervals where regulation deployment was both up and down for peak hours.
Track the Regulation exhaustion rate for all hours (not to exceed 5%).
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours.

## Slide 10: Total Regulation Deployed Comparison
Total regulation deployed for the last three months.

## Slide 11: Total Regulation Deployed Comparison - Monthly
Notes: Total regulation deployed comparison in the last 3 months: Overall the trends have been very similar. A bit more reg up deployment during in the middle of the day due to higher than expected load.

## Slide 12: Metric 1: Regulation Deployed Comparisons
Trend and monitor the regulation deployed by hour.

## Slide 13: Regulation Deployed Comparison

## Slide 14: Regulation Deployed Comparison
Notes: More reg up deployment from mid day to sunset due to high load and solar ramps.

## Slide 15: Regulation Deployed Comparison
Notes: Overall Regulation down deployment in June is consistent with that of previous two years. The jump in HE9 is due to morning solar ramp.

## Slide 16: Metric 2: Total Regulation Deployed Comparisons
Set target of 50MW for total regulation deployed by hour for peak hours.

## Slide 17: Total Regulation Deployed Comparison
Chart: Total Regulation Deployed
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | -84.7922 | -89.0969 | -74.0651 | -45.5097 | -22.972 | -20.4255 | 6.9291 | 25.3448 | -21.6806 | -13.1201 | 42.8744 | 62.3261 | 64.4754 | 64.036 | 42.1414 | 24.0637 | 5.844 | 33.1342 | 79.4842 | -117.9775 | -140.1178 | -82.3421 | -71.5243 | -106.6171
Oct-21 | -58.8685 | -58.4787 | -48.2325 | -40.5796 | -20.3955 | -35.1242 | 35.7371 | 6.1027 | -77.3982 | -12.7121 | 11.8488 | 1.6039 | 10.8454 | 7.2803 | 2.987 | -7.901 | -67.6932 | -47.2422 | 87.2093 | -166.5157 | -108.1902 | -77.9862 | -62.0246 | -57.6496
Oct-22 | -57.4311 | -80.9564 | -70.5699 | -49.0399 | -25.2646 | -1.1162 | 32.7742 | 16.6523 | -110.3824 | -26.7519 | 9.4537 | 24.3574 | -5.8088 | 13.4664 | 33.2502 | 7.5019 | -13.7585 | 95.9122 | 140.9262 | -99.8448 | -75.3028 | -71.0724 | -69.4458 | -69.1271
Threshold (50MW) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Notes: Total regulation deployed compared with pervious two year. More reg up deployed during sunset and more reg down deployed due to sun rise.

## Slide 18: Metric 3: 15-min Intervals Where Both REGUP/REGDN Were Deployed
Set target of 85% for the number of intervals where regulation deployment was both up and down.

## Slide 19: “Zero” Crossing Regulation
Notes: For zero crossing regulation usage, the smaller zero-crossing reg percentages occurred during sun rise and sun set hours.

## Slide 20: “Zero” Crossing Regulation
Notes: Overall, we see that it is over 68% for all hours, which shows a good balance of deploying both Reg up and down.

## Slide 21: Metric 4: Regulation Exhaustion Rate
Track the regulation exhaustion rate for all hours (not to exceed 5%.)

## Slide 22: Regulation Exhaustion Rate
Chart: Regulation-Up Exhaustion Rate
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | 0.026882 | 0.010753 | 0.024194 | 0.010753 | 0.0053763 | 0 | 0 | 0.021505 | 0.0026882 | 0.013441 | 0.010753 | 0.0053763 | 0 | 0.021505 | 0.018817 | 0.037634 | 0.018817 | 0.14516 | 0.12634 | 0.016129 | 0.0026882 | 0.02957 | 0.043011 | 0.018817
Oct-21 | 0.086022 | 0.024194 | 0.040323 | 0.021505 | 0.0053763 | 0 | 0 | 0.0053763 | 0.0026882 | 0.010753 | 0.0053763 | 0 | 0 | 0.0026882 | 0.0080645 | 0.0026882 | 0.0053763 | 0.02957 | 0.13978 | 0.024194 | 0.021505 | 0.037634 | 0.072581 | 0.072581
Oct-22 | 0.037634 | 0.016129 | 0.02957 | 0.010753 | 0.0026882 | 0.0080645 | 0.0026882 | 0.0053763 | 0 | 0.0053763 | 0 | 0 | 0 | 0 | 0.0080645 | 0.0053763 | 0.0026882 | 0.010753 | 0.024194 | 0.0026882 | 0.021505 | 0.05914 | 0.040323 | 0.02957
Notes: Average regulation up exhaustion rate for all hours is 2.58 %

## Slide 23: Regulation Exhaustion Rate
Chart: Regulation-Down Exhaustion Rate
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | 0.0080645 | 0.077957 | 0.08871 | 0.25806 | 0.14785 | 0.018817 | 0.061828 | 0.018817 | 0.27957 | 0.037634 | 0.040323 | 0.018817 | 0.026882 | 0.040323 | 0.032258 | 0.048387 | 0.021505 | 0.0026882 | 0 | 0.056452 | 0.016129 | 0 | 0 | 0
Oct-21 | 0.010753 | 0.034946 | 0.069892 | 0.10753 | 0.20161 | 0.086022 | 0.099462 | 0.02957 | 0.16398 | 0.048387 | 0.056452 | 0.053763 | 0.013441 | 0.045699 | 0.032258 | 0.032258 | 0.02957 | 0.051075 | 0.0080645 | 0.19086 | 0.018817 | 0 | 0.0026882 | 0.0026882
Oct-22 | 0.010753 | 0.053763 | 0.11022 | 0.13441 | 0.077957 | 0.037634 | 0.08871 | 0.037634 | 0.096774 | 0.034946 | 0.048387 | 0.051075 | 0.045699 | 0.05914 | 0.026882 | 0.051075 | 0.0080645 | 0.018817 | 0.013441 | 0.018817 | 0 | 0.010753 | 0 | 0.0080645
Notes: Average regulation down exhaustion rate for all hours is 9.8 %

## Slide 24: Metric 5: Stats on REGUP Bias for Consecutive 5-min Intervals
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5-minute intervals for peak hours.

## Slide 25: Regulation Bias for Consecutive SCED Intervals
Chart: Regulation-Up Bias
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | 1 | 0 | 0 | 0 | 0 | 2 | 1 | 3 | 2 | 5 | 5 | 8 | 8 | 6 | 6 | 5 | 1 | 9 | 10 | 1 | 1 | 0 | 1 | 0
Oct-21 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 4 | 5 | 2 | 1 | 1 | 3 | 1 | 0 | 3 | 15 | 1 | 0 | 0 | 0 | 0
Oct-22 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 1 | 0 | 5 | 5 | 6 | 3 | 5 | 6 | 5 | 1 | 9 | 16 | 1 | 2 | 0 | 1 | 1
Notes: Regulation up bias occurrence for consecutive SCED intervals for all hour is 133 and peak hours is 48.

## Slide 26: Regulation Bias for Consecutive SCED Intervals
Chart: Regulation-Down Bias
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | 9 | 9 | 12 | 8 | 5 | 2 | 2 | 2 | 16 | 7 | 0 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 20 | 17 | 7 | 10 | 13
Oct-21 | 7 | 4 | 5 | 8 | 7 | 3 | 3 | 2 | 10 | 8 | 4 | 4 | 4 | 3 | 1 | 2 | 8 | 7 | 0 | 20 | 7 | 8 | 8 | 8
Oct-22 | 9 | 9 | 9 | 4 | 3 | 4 | 4 | 1 | 16 | 6 | 4 | 3 | 6 | 4 | 1 | 3 | 2 | 3 | 1 | 12 | 5 | 11 | 5 | 7
Notes: Regulation down bias occurrence for consecutive SCED intervals for all hour is 160 and peak hours is 12.

## Slide 27: Time Error and Contributing Factors
Accumulated Time Error, Load and Wind Ramp, PWRR Error, Start-Up/Shut-Down Hours, STLF Error, and Expected Generation Deviation.

## Slide 28: Time Error Accumulation
Chart: Hourly Accumulated Time Error
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | 0.0090001 | 6.034 | 5.396 | 9.965 | 7.277 | 1.013 | 2.251 | -3.65 | 11.208 | -2.505 | -2.727 | -2.959 | -2.048 | -3.617 | -4.738 | -5.713 | -2.908 | -14.068 | -9.039 | 3.26 | 4.478 | 0.574 | -1.759 | 3.496
Oct-21 | -5.642 | 1.626 | 1.19 | 3.55 | 6.366 | 1.806 | 0.314 | 0.328 | 6.483 | -2.864 | -1.065 | -1.519 | -1.298 | -0.778 | -1.414 | -0.763 | 0.578 | -1.375 | -10.469 | 7.449 | 1.509 | -0.174 | -1.371 | -1.814
Oct-22 | -1.118 | 3.04 | 3.419 | 3.552 | 1.769 | -1.031 | 0.575 | 1.19 | 3.223 | -1.052 | -0.811 | -0.60082 | -0.391 | -0.538 | -2.204 | -0.894 | -1.258 | -4.394 | -0.473 | 2.467 | -0.736 | -3.229 | -2.259 | 1.625
Notes: Hourly time error accumulation is fairly similar compared with last years.

## Slide 29: Load Profile
Chart: ERCOT Total Hourly Load
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | 36983.4641 | 35433.9482 | 34446.9016 | 33922.5157 | 34012.5277 | 35026.4379 | 36982.479 | 38279.7243 | 39143.1686 | 40517.2647 | 42084.8534 | 43730.5603 | 45379.8734 | 47011.3802 | 48337.0968 | 49308.8419 | 49850.8131 | 49495.9712 | 48211.4076 | 47539.472 | 46164.1786 | 44188.5975 | 41674.8049 | 39009.4388
Oct-21 | 38760.1343 | 37081.3984 | 35976.9481 | 35371.7193 | 35382.9582 | 36302.4434 | 38201.2994 | 39374.0253 | 40189.4776 | 41822.1678 | 43691.7011 | 45586.4873 | 47463.1394 | 49398.6846 | 51008.1778 | 52231.8874 | 52933.0336 | 52545.1456 | 50918.8826 | 49968.4016 | 48484.6733 | 46406.7593 | 43687.0751 | 40846.9114
Oct-22 | 38472.1545 | 36902.4858 | 35892.8982 | 35336.2562 | 35402.3704 | 36398.0938 | 38292.0094 | 39391.7529 | 40102.8815 | 41560.814 | 43070.5693 | 44602.7516 | 46233.3013 | 47958.5766 | 49458.4386 | 50750.4043 | 51577.5644 | 51388.5609 | 50033.2873 | 49221.9883 | 47957.5303 | 45994.3589 | 43350.6817 | 40571.4965
Notes: There is a big increase in total load in July due to high temperatures.

## Slide 30: Net Load Profile
Chart: ERCOT Total Hourly Load
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | 36983.4641 | 35433.9482 | 34446.9016 | 33922.5157 | 34012.5277 | 35026.4379 | 36982.479 | 38279.7243 | 39143.1686 | 40517.2647 | 42084.8534 | 43730.5603 | 45379.8734 | 47011.3802 | 48337.0968 | 49308.8419 | 49850.8131 | 49495.9712 | 48211.4076 | 47539.472 | 46164.1786 | 44188.5975 | 41674.8049 | 39009.4388
Oct-21 | 38760.1343 | 37081.3984 | 35976.9481 | 35371.7193 | 35382.9582 | 36302.4434 | 38201.2994 | 39374.0253 | 40189.4776 | 41822.1678 | 43691.7011 | 45586.4873 | 47463.1394 | 49398.6846 | 51008.1778 | 52231.8874 | 52933.0336 | 52545.1456 | 50918.8826 | 49968.4016 | 48484.6733 | 46406.7593 | 43687.0751 | 40846.9114
Oct-22 | 38472.1545 | 36902.4858 | 35892.8982 | 35336.2562 | 35402.3704 | 36398.0938 | 38292.0094 | 39391.7529 | 40102.8815 | 41560.814 | 43070.5693 | 44602.7516 | 46233.3013 | 47958.5766 | 49458.4386 | 50750.4043 | 51577.5644 | 51388.5609 | 50033.2873 | 49221.9883 | 47957.5303 | 45994.3589 | 43350.6817 | 40571.4965
Oct-20 | 24792.9701 | 23479.8491 | 22809.1382 | 22587.8216 | 22909.9539 | 24227.5087 | 26456.0488 | 27987.6512 | 28936.4971 | 30254.0789 | 31673.0763 | 33380.9387 | 35226.2129 | 36948.4505 | 38240.0338 | 39062.9905 | 39492.9612 | 39339.4207 | 39188.6168 | 38607.9378 | 35676.0882 | 32638.4539 | 29648.0322 | 26810.7438
Oct-21 | 24727.912 | 23307.0244 | 22549.2326 | 22455.0652 | 22837.1244 | 24116.4881 | 26376.0087 | 27898.2982 | 28215.5802 | 28731.5509 | 30044.8411 | 31362.0398 | 33105.7288 | 35000.2523 | 36394.1967 | 37367.2699 | 37913.2954 | 37903.7347 | 38560.1457 | 38335.7142 | 35227.8472 | 32322.8341 | 29333.5558 | 26417.7779
Oct-22 | 25968.6044 | 24650.1096 | 24020.5514 | 23999.6219 | 24362.5896 | 25579.0175 | 27698.727 | 29174.4659 | 28699.5406 | 28130.1236 | 28464.9256 | 29504.7022 | 31029.0665 | 32636.9836 | 34057.1635 | 35192.6764 | 36256.9213 | 37448.2963 | 39591.5353 | 39736.8823 | 37083.699 | 34122.5496 | 30976.0073 | 28041.4216
Notes: The netload peak in July is also higher than that of last two years

## Slide 31: Load Ramp
Chart: ERCOT Hourly Load Ramp
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | -1832.983 | -1262.4387 | -768.6735 | -281.6016 | 413.5041 | 1549.697 | 2035.0316 | 710.2574 | 1230.9744 | 1498.6753 | 1613.5209 | 1663.6949 | 1670.1072 | 1493.376 | 1158.155 | 846.4333 | 128.8954 | -793.8128 | -1272.3959 | -706.2739 | -1817.7549 | -2221.5713 | -2674.7693 | -2492.2981
Oct-21 | -2052.7387 | -1375.6234 | -857.7885 | -347.2875 | 322.6995 | 1418.3463 | 2061.5539 | 483.7809 | 1366.5321 | 1798.6804 | 1916.9307 | 1865.1142 | 1947.8564 | 1829.3506 | 1395.8726 | 1059.6319 | 248.3516 | -1005.7496 | -1641.3952 | -936.4567 | -1841.0378 | -2388.7848 | -2846.9549 | -2692.7666
Oct-22 | -1935.3488 | -1331.9086 | -747.328 | -315.1937 | 399.3164 | 1515.9833 | 1993.5459 | 366.6623 | 1209.2096 | 1555.636 | 1582.2118 | 1565.9577 | 1718.2206 | 1657.7051 | 1387.2075 | 1165.8623 | 363.2762 | -772.3528 | -1395.3591 | -790.6654 | -1691.3894 | -2263.0741 | -2751.2984 | -2602.625
Notes: Hourly load ramp is higher in the middle of the day compared to last two years’.

## Slide 32: Wind Profile
Chart: ERCOT Wind Profile
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | 12190.4097 | 11954.0426 | 11637.7077 | 11334.5457 | 11102.5018 | 10798.8716 | 10526.3582 | 10290.0396 | 9750.8027 | 8527.6274 | 8262.5047 | 8054.2236 | 7763.5736 | 7611.6961 | 7570.8061 | 7681.157 | 7835.1048 | 8043.1777 | 8229.8759 | 8912.1321 | 10488.0205 | 11550.0547 | 12026.7002 | 12198.6258
Oct-21 | 14027.7435 | 13769.8734 | 13423.2299 | 12912.1631 | 12542.8013 | 12185.8168 | 11825.1565 | 11465.7211 | 10892.9023 | 9247.3591 | 8965.2357 | 9169.3699 | 9114.2281 | 9209.6019 | 9535.3474 | 9860.5983 | 10195.5065 | 10637.4528 | 10844.7761 | 11591.9745 | 13252.2216 | 14079.3792 | 14349.0115 | 14424.6292
Oct-22 | 12503.1283 | 12251.9577 | 11871.9282 | 11336.2289 | 11039.3496 | 10818.6596 | 10592.8578 | 10171.1128 | 9501.7838 | 7723.2789 | 7447.2795 | 7639.039 | 7615.6274 | 7780.3657 | 7947.2999 | 8285.4604 | 8671.789 | 8828.2031 | 8860.2906 | 9432.4692 | 10868.2854 | 11871.1096 | 12374.2122 | 12529.6628
Notes: Hourly wind generation is much higher compared to the last two years’.

## Slide 33: Start-Up & Shut-Down Hours
Chart: Net Capacity on Start-Up/Shut-Down
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | -1079.0707 | -658.1439 | -196.0141 | 138.382 | 907.7224 | 2745.64 | 817.5252 | 600.4818 | 1215.716 | 836.1838 | 1169.1287 | 1144.9802 | 947.6501 | 822.483 | 673.3551 | 385.2756 | 182.7021 | 57.3816 | -300.0119 | -829.3004 | -1977.1364 | -1830.3418 | -2066.9989 | -1873.3381
Oct-21 | -1467.0936 | -374.3697 | -151.5563 | 343.9693 | 1116.7754 | 3055.9651 | 994.2764 | 761.819 | 1102.8777 | 1175.6282 | 1650.2274 | 2013.1957 | 1453.301 | 1273.2523 | 871.5826 | 631.5108 | 282.7986 | 43.9666 | 38.9449 | -578.2867 | -1607.4003 | -2830.2737 | -3901.2356 | -3339.0135
Oct-22 | -972.2548 | -239.0799 | -36.2303 | -64.8755 | 753.9849 | 2031.0553 | 224.8191 | 408.841 | 450.3465 | 276.5191 | 1756.8121 | 2234.4586 | 2087.993 | 1172.0778 | 953.3279 | 778.9597 | 886.7826 | 551.5274 | 321.053 | -202.1752 | -1788.6633 | -3019.414 | -2974.1524 | -2841.9521
Notes: Net capacity on start up and shut down is fairly consistent with last two years.

## Slide 34: Short-Term Load Forecast Error
Chart: Short-Term Load Forecast Error
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | 10.0169 | 12.4441 | 11.9142 | 10.8133 | 14.5347 | 25.0282 | 30.1358 | -38.2214 | -19.6841 | -18.247 | -27.6116 | -33.2913 | -27.3735 | -21.4139 | -15.6343 | -5.7776 | 3.3558 | 2.0226 | 27.0461 | 26.66 | 16.0281 | 0.59141 | -4.0888 | 3.5233
Oct-21 | 15.0326 | 6.7999 | 6.4226 | 2.4644 | 1.726 | 6.8043 | -3.9771 | -7.7763 | 0.56467 | -3.6438 | -10.0081 | -8.0511 | -10.9942 | -17.0798 | -12.2716 | -12.7813 | -11.8628 | 3.5467 | 29.1894 | 13.9391 | -0.26607 | 3.9374 | 4.9708 | 3.224
Oct-22 | 5.5019 | 0.69896 | 0.14201 | -0.47816 | 0.099898 | -1.0627 | 5.5299 | 1.2528 | 1.5388 | -2.7861 | -0.068559 | 10.9025 | 6.5467 | -3.277 | -7.7497 | -16.714 | -17.7494 | -8.1047 | 5.3169 | 5.4612 | -14.0597 | -3.5278 | -0.55256 | 0.36313
Notes: Forecast – Actual
+ve Error => Over forecasted load
-ve Error +> Under forecasted load
For STLF, we have seen over-forecast during daytime and under-foreacast during night time.

## Slide 35: STLF Error Chart
Chart: STLF Error
Notes: Error = Forecast – Actual
Min,Max, 10th, 90th percentile
15 minute intervals
Max Positive Forecast Error:
8/10/2022 19:00 -> 337.7 MW
Max Negative Forecast Error:
8/23/2022 17:45 -> -211 MW

## Slide 36: Expected Generation Deviation
Chart: Expected Generation Deviation
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Oct-20 | -21.052 | -19.1094 | -38.0155 | -54.344 | -52.3793 | -67.421 | -101.3886 | -63.6359 | -38.6212 | -40.9403 | -46.3674 | -106.3391 | -123.37 | -135.2865 | -123.5146 | -111.6077 | -97.3629 | -160.8376 | -250.3988 | 70.1358 | 151.88 | 63.7633 | 2.0321 | 28.1964
Oct-21 | -81.9956 | -49.5442 | -74.5418 | -74.3431 | -75.902 | -79.3291 | -143.3377 | -74.6463 | 97.8888 | 17.2596 | 2.646 | -56.8666 | -100.4683 | -82.1108 | -69.5453 | -75.1706 | -52.1621 | -178.6142 | -471.4795 | 58.8513 | 134.0723 | 39.6015 | -6.0229 | -36.8901
Oct-22 | -60.6279 | -24.8156 | -38.817 | -50.7938 | -47.0068 | -104.3179 | -129.4679 | -62.0943 | 188.0902 | 65.0617 | 24.8832 | -78.6616 | -53.6122 | -85.1228 | -122.5211 | -92.0818 | -150.3923 | -376.5955 | -452.1361 | 14.1098 | 109.2079 | 43.2149 | 16.0025 | -6.7489

## Slide 37: Expected Generation Deviation
Notes: Breakdown by resource type and we see significant contribution from wind and solar during the ramping hours

## Slide 38: Expected Generation Deviation
Notes: Comparing renewables vs non-renewables. Again, IRR resources are the main contributor for most part of the day.

## Slide 39: Questions?
Thank you!