## Slide 1
Use of EMS Computed TLFs in Settlements vs. Seasonal Base Case TLFs
WMWG
June 17, 2022
Randy Roberts

## Slide 2: Current Seasonal Process
In place since zonal market inception
Requires ERCOT-wide calculation and separate calculation for 9 NOIEs who have bi-directional boundary metering configurations where the metered value includes losses from the NOIE transmission system
  NOIEs are AEN, BPUB, BTU, COCS, COD, COG, CPS, GEUS, & LP&L
    NOTE: LP&L planning to open their area to competition and at that time will no longer be included in list above
NOIE Factors are used to reduce NOIE load to account for the behind-the-meter transmission losses, prior to application of ERCOT-wide “postage stamp” TLFs
Factors are derived from ERCOT seasonal base case studies (it is important to note the studies use a static system configuration for each season)
  For each season, a slope & intercept is calculated using the on-peak and off-peak load values
Seasonal slope and intercept values are loaded into ERCOT settlement system
  ERCOT-wide and for the 9 NOIEs
Settlement system then computes the ERCOT-wide loss factor percentage for each interval using the actual load from ERCOT EMS system. NOIE percentages are calculated using NOIE settlement load volumes as computed during the data aggregation process.
Calculated interval TLFs are then applied to load during the data aggregation process

## Slide 3: Current Requirement to Use Deemed Actual for Settlement
Protocol 13.2.2 – Deemed Actual Transmission Loss Factors
  (1) ERCOT shall determine the deemed actual TLF for each interval in the Operating Day, by use of a linear interpolation or extrapolation using the on-peak and the off- peak TLFs corresponding to the actual ERCOT System Load during the interval.
  (2) The day after the Operating Day, ERCOT shall calculate deemed actual TLFs for each Settlement Interval of the Operating Day and publish the TLFs to be used in Settlement calculations.
  (3) ERCOT shall use the TLFs corresponding to the on-peak and off-peak base case ERCOT System Loads during the applicable seasons as the basis for the ERCOT- wide deemed actual TLFs. ERCOT will post TLFs to the MIS Public Area by 0600 two days after the Operating Day.

## Slide 4: Deemed Actual/Forecasted Calculation Details
Protocol 13.2.3 – Transmission Loss Factor Calculations
  The following formulas shall be used to translate the seasonal on-peak and off-peak TLFs into Settlement Interval TLFs.
    TLFi = (SSC * SIELi) + SIC
    And
    SSC = (SONLF – SOFFLF)/(SONL-SOFFL)
    SIC = [(SOFFLF*SONL)-(SONLF*SOFFL)]/(SONL-SOFFL)
Variable | Unit | Description
i | none | Interval
TLFi | none | Transmission Loss Factor for a Settlement Interval
SIELi | MWh | Settlement Interval ERCOT System Load (forecasted or actual)
SSC | none | Seasonal Slope Coefficient
SIC | none | Seasonal Intercept Coefficient
Variable | Unit | Description
SONLF | none | Seasonal on-peak percent loss factor
SOFFLF | none | Seasonal off-peak percent loss factor
SONL | none | Seasonal on-peak Load value
SOFFL | none | Seasonal off-peak Load value

## Slide 5: TLF Chart (linear interpolation or extrapolation)

## Slide 6: Posting Requirements
Protocol 13.1.1 – Responsibility for Transmission and Distribution Losses
  (2) ERCOT shall forecast Transmission Loss Factors (TLFs) and post them to the ERCOT website by 0600 of the Day-Ahead period. ERCOT shall forecast the ERCOT-wide TLFs as a percentage of Load for each Settlement Interval of the Operating Day. By the close of business on the day following the Operating Day, ERCOT shall also calculate TLFs for each Settlement Interval using the actual system Load for that Settlement Interval and shall post the resulting deemed actual TLFs to the settlement system and the ERCOT website.

## Slide 7: Methodology for Calculating Losses in EMS
Power (MW) Losses in Transmission Lines and Transformers are calculated in EMS as
IN – POUT
In the example below:
Power Loss is calculated as A – PB
Where PA = MW flowing into the line at Station A
PB = MW flowing out of the line at Station B
The ERCOT Loss Ratio is calculated as:

## Slide 8: Hourly TLFs

## Slide 9: Hourly UFE

## Slide 10: EMS vs. Seasonal Comparison and Resultant UFE Change

## Slide 11: Summary/Conclusion
Changing the TLF methodology will not change the volume of settled load
  That is because after the TLF application process, we apply UFE which forces the settled load to match the metered generation. However, the new methodology would modify the load volumes produced by the TLF application process resulting in new load volume inputs to the UFE process (essentially shifting load from one to the other). Additionally, TLFs are applied to all load whereas UFE is only applied to competitive load.
Current process has a tendency to narrow the bandwidth of TLFs vs. EMS computed values, which in turn increases the bandwidth of %UFE
Use of computed EMS factors would result in more TLF bandwidth and less %UFE bandwidth
Use of computed EMS factors would result in more accurate settlements
Additional considerations
  Does EMS system need to add data quality flags or estimation routines
  Does Data Agg process need to add an EMS TLF smoothing routine

## Slide 12: Options for Moving Forward
NPRR1145 if approved would implement item 1
Use EMS computed ERCOT-wide TLFs for Settlement with no other changes
  Seasonal TLFs would still be used for NOIE load reduction (≈12% of ERCOT Load)
  Posted forecast TLFs would remain seasonal
Use EMS computed ERCOT-wide TLFs for Settlement and create a new process to produce forecasted ERCOT-wide EMS TLFs
  Seasonal TLFs would still be used for NOIE load reduction (≈12% of ERCOT Load)
Use EMS computed ERCOT-wide & NOIE TLFs for Settlement and create a new process to produce forecasted ERCOT-wide EMS TLFs
  Would require placement of NOIE tie meters into the model and a new equipment/line attribute so that each NOIEs behind-the-meter losses can be calculated