## Slide 1
Dec 5, 2022
TAC
ERCOT Staff
Proposed 2023 Ancillary Service Methodology And Preliminary Quantities

## Slide 2: Stakeholder Discussion Timeline
September 14, 2022 – PDCWG (Methodology Discussion)
September 23, 2022 – WMWG (Methodology Discussion)
October 21, 2022 – WMWG (Proposed Methodology)
October 27, 2022 – OWG (Proposed Methodology)
October 28, 2022 – PDCWG (Proposed Methodology)
November 02, 2022 - WMS
November 07, 2022 - ROS
December 5, 2022 - TAC
December 20, 2022 – BoD

## Slide 3: Introduction
This presentation will provide a summary of the proposed methodology for computing Ancillary Service (A/S) quantities in 2023.
  ERCOT is not proposing any changes in the methodologies used to compute Regulation Service and Responsive Reserve Service (RRS) requirements for 2023.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2023 assessment for ERCOT shows an increase in ERCOT’s IFRO. To align with ERCOT’s 2023 IFRO, minimum RRS-PFR limit for 2023 will change to 1,390 MW.
  ERCOT is proposing some changes in the methodology used to compute minimum Non-Spinning Reserve Service (Non-Spin) requirements in 2023. Specifically,
    Prior to ECRS: Use 85th to 95th percentile of 10 Hours Ahead (HA) max. net load forecast error
    After ECRS: Use 75th to 95th percentile of 6 HA hourly avg. net load forecast error
  Upon its implementation, ERCOT is proposing to compute ECRS requirements as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support sustained net load ramps.
    Per the Nov 11 PRS | Project Update, ECRS is currently scheduled for 2023 R3 (5/23 – 5/25) release.
Spreadsheets that contain the preliminary quantities for 2023 computed using the proposed methodology and a redline version of the A/S Methodology document have been posted on today’s meeting page.

## Slide 4: Non-Spinning Reserve Methodology - 2023
ERCOT is proposing changes in the methodology used to compute minimum Non-Spin requirements in 2023,
  Before ECRS is implemented: Use 85th to 95th percentile of 10 HA max. net load forecast error
  After ECRS* is implemented: Use 75th to 95th percentile of 6 HA hourly avg. net load forecast error
  The preliminary Non-Spin quantities have been computed using 2020, 2021 and 2022 Net load and Net load Forecast, updated Wind and Solar Over-Forecast Error Adjustment tables and the updated Intra-day Outage table**.
  Lastly, in 2023, ERCOT will continue the practice of monitoring the weather near Real Time and may procure up to an additional 1,000 MW of Non-Spin for specific Operating Hours.
*Note that per the Nov 11 PRS | Project Update, ECRS is currently scheduled for 2023 R3 (5/23 – 5/25) release.
**Wind and Solar Over-Forecast Error Adjustment Table track estimated increase in wind and solar over forecast error per 1000 MW increase in installed wind and solar capacity, respectively. The Intra-day Outage table accounts for increased capacity needs following forced outages of thermal resources within an operating day.

## Slide 5: ECRS Requirements Methodology - 2023
In 2023, ERCOT is proposing to compute ECRS requirements as the sum of capacity needed to
  Recover Frequency following a large unit trip:
    For various inertia levels, a medium-sized supply-side resource is tripped such that frequency nadir is just above 59.7 Hz and amount of response needed to return frequency to 59.98 Hz is determined.
  Support Intra-Hour Net Load Forecast errors:
    85th – 95th percentile of 30-minute ahead intra-hour netload forecast errors for last two years. The percentile is associated with the risk of net load ramp. The larger the netload ramp, the higher the percentile.
    An additional adjustment will be included to account for the impact of increase in the solar generation installed capacity on the intra hour net load forecast error.
*Note that per the Nov 11 PRS | Project Update, ECRS is currently scheduled for 2023 R3 (5/23 – 5/25) release.
**Solar Intra-Hour Over-Forecast Error Adjustment Table track estimated increase in solar over forecast error per 1000 MW increase in installed solar capacity.

## Slide 6: Summary
In summary,
  ERCOT is not proposing any changes in the methodologies used to compute Regulation Service and RRS requirements for 2023.
  To align with in ERCOT’s 2023 IFRO, minimum RRS-PFR limit for 2023 will change to 1,390 MW.
  ERCOT is proposing changes in the methodology used to compute minimum Non-Spin requirements in 2023. Specifically,
    Prior to ECRS: Use 85th to 95th percentile of 10 Hours Ahead (HA) max. net load forecast error
    After ECRS: Use 75th to 95th percentile of 6 HA hourly avg. net load forecast error
  Upon its implementation, ERCOT is proposing to compute ECRS requirements as the sum of capacity needed to recover frequency following a large unit trip and capacity needed to support sustained net load ramps.
ERCOT is requesting TAC’s endorsement of the 2023 A/S Methodology.

## Slide 7
Suggestions?

## Slide 8: 2023 Solar Adjustment Tables
Solar Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed solar capacity. The methodology for 2023 Solar Adjustment tables has been updated to better align it with how 5-minute wind and solar forecasted ramps are currently used in operations.
 | Min (MW) | Max (MW) | Average (MW)
Reg Up | 0 | 25.4 | 9.9
Reg Down | 0 | 22.4 | 8.2

## Slide 9: 2023 Wind Adjustment Tables
Wind Adjustment Tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind capacity.
Notes: Avg Reg Up adjustment for wind is 1.57 MW
Avg Reg Down adjustment for wind is 1.44 MW

## Slide 10: Regulation Service Methodology
ERCOT is not proposing any change to the methodology used to compute the minimum Regulation Service requirements in 2023.
  The preliminary Regulation quantities have been computed using 2021 and 2022 five-minute net load variability, updated Wind Adjustment and Solar Adjustment tables*.
*Wind and Solar Adjustment tables track incremental MWs of Regulation needed to account for additional variability per 1000 MW increase in installed wind and solar capacity, respectively.

## Slide 11: 2023 RRS Table
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
*RRS Curr IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3088 | 3015 | 2982 | 2936 | 2898 | 2825 | 2732 | 2668
**RRS Upd IFRO (MW) | 3335 | 3287 | 3239 | 3195 | 3156 | 3079 | 3041 | 2991 | 2949 | 2871 | 2774 | 2705
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS Curr IFRO (MW) | 2618 | 2571 | 2538 | 2498 | 2450 | 2416 | 2375 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068
**RRS Upd IFRO (MW) | 2651 | 2600 | 2562 | 2517 | 2466 | 2427 | 2381 | 2344 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,240 MW.
**RRS quantity is calculated for RCC of 2805 with limit of 60% limit on LRs and min RRS-PFR limit of 1,390 MW.
***Red font in table above identifies study scenario where RRS needed < 2300 MW. RRS requirement during these is based on the applicable floor.
****Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest
Notes: RRS quantity for 2022 decrease between 8 MW (310 GW.s case) and 82 MW (170 GW.s case)

## Slide 12: Responsive Reserve Service (RRS) Methodology
ERCOT is not proposing any change to methodology used to compute the minimum RRS requirements for 2023.
  The preliminary RRS quantities have been computed using 2021 and 2022 system inertia conditions and updated RRS table*.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2023 assessment for ERCOT shows an increase in ERCOT’s IFRO. To align with ERCOT’s 2023 IFRO, minimum RRS-PFR limit for 2023 will change to 1,390 MW.
*The RRS table tracks RRS requirements for different inertia conditions. This table was updated in 2023 to use a minimum RRS-PFR limit of 1,390 MW.
Notes: OY2022 IFRO – 412 MW/0.1 Hz | Limit 1,240 MW
OY2023 IFRO – 463 MW/0.1 Hz | Limit 1,390 MW

## Slide 13: 2023 Intra-day Outage Table
The Intra-day Outage table helps account for increased capacity needs following forced outages of thermal resources within an operating day.

## Slide 14: ECRS Adjustment for Increase in Solar Installed Capacity
Intra-hour Solar Over-Forecast Error Adjustment Table tracks estimated increase in 30-min ahead solar over forecast error per 1000 MW increase in installed solar capacity.
Additional ECRS per 1,000 MW increase in solar installed capacity
Adjustment for 2023 (Min: 0 MW | Mean: 64 MW | Max 283 MW)