## 2023 RRS Table
| Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12 |  | LR/PFR ER | Inertia (MW) | PFR Requirement | LR Requirement | RRS
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1 |  | 3.3 | 122 | 1413 | 2121 | 3534
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 |  | 2.35 | 130 | 1390 | 1945 | 3293
PFR Req. (no LR) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139 |  | 2.2 | 140 | 1390 | 1897 | 3234
(MW) | [13 empty] | 2.06 | 150 | 1390 | 1849 | 3178
*RRS Curr IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3088 | 3015 | 2982 | 2936 | 2898 | 2825 | 2732 | 2668 |  | 1.94 | 160 | 1390 | 1805 | 3128
**RRS Upd IFRO (MW) | 3293 | 3234 | 3178 | 3128 | 3088 | 3015 | 2982 | 2936 | 2898 | 2825 | 2732 | 2668 |  | 1.83 | 170 | 1390 | 1766 | 3088
[14 empty] | 1.74 | 180 | 1390 | 1689 | 3015
| Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25 | 1.65 | 190 | 1390 | 1651 | 2982
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:01 | 1:01 | 1:01 | 1:01 | 1:01 | 1.58 | 200 | 1390 | 1601 | 2936
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370 | 1.51 | 210 | 1390 | 1559 | 2898
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068 | 1.44 | 220 | 1390 | 1481 | 2825
*RRS Curr IFRO (MW) | 2618 | 2571 | 2538 | 2498 | 2450 | 2416 | 2375 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068 | 1.39 | 230 | 1390 | 1384 | 2732
**RRS Upd IFRO (MW) | 2618 | 2571 | 2538 | 2498 | 2450 | 2416 | 2375 | 2342 | 2290 | 2230 | 2173 | 2119 | 2068 | 1.33 | 240 | 1390 | 1315 | 2668
[14 empty] | 1.28 | 250 | 1390 | 1261 | 2618
[14 empty] | 1.24 | 260 | 1390 | 1210 | 2571
[14 empty] | 1.19 | 270 | 1390 | 1172 | 2538
[14 empty] | 1.15 | 280 | 1390 | 1127 | 2498
[14 empty] | 1.12 | 290 | 1390 | 1076 | 2450
[14 empty] | 1.08 | 300 | 1390 | 1037 | 2416
[14 empty] | 1.04 | 310 | 1390 | 991 | 2375
[14 empty] | 1.01 | 320 | 1390 | 954 | 2342
[14 empty] | 1 | 330 | 1390 | 900 | 2290
[14 empty] | 1 | 340 | 1390 | 840 | 2230
[14 empty] | 1 | 350 | 1390 | 783 | 2173
[14 empty] | 1 | 360 | 1390 | 729 | 2119
[14 empty] | 1 | 370 | 1390 | 678 | 2068

## 2022_RRS
2022 RRS (Floor = 2800 MW for peak hours ¦ Floor = 2300 MW for remaining hours, New IFRO=1240 MW)
HE | Jan | Feb | Mar | Apr | May | Jun | July | Aug | Sep | Oct | Nov | Dec
1 | 2982 | 3015 | 3178 | 3088 | 2982 | 2668 | 2498 | 2498 | 2732 | 2982 | 3178 | 3128
2 | 2982 | 3015 | 3178 | 3088 | 2982 | 2668 | 2498 | 2498 | 2732 | 2982 | 3178 | 3128
3 | 2982 | 3015 | 3178 | 3128 | 3015 | 2825 | 2538 | 2538 | 2825 | 3015 | 3178 | 3088
4 | 2982 | 3015 | 3178 | 3128 | 3015 | 2825 | 2538 | 2538 | 2825 | 3015 | 3178 | 3088
5 | 2982 | 3015 | 3178 | 3128 | 3015 | 2825 | 2538 | 2538 | 2825 | 3015 | 3178 | 3088
6 | 2982 | 3015 | 3178 | 3128 | 3015 | 2825 | 2538 | 2538 | 2825 | 3015 | 3178 | 3088
7 | 2898 | 2898 | 3088 | 3015 | 2936 | 2618 | 2450 | 2498 | 2618 | 2936 | 3015 | 3015
8 | 2898 | 2898 | 3088 | 3015 | 2936 | 2618 | 2450 | 2498 | 2618 | 2936 | 3015 | 3015
9 | 2898 | 2898 | 3088 | 3015 | 2936 | 2618 | 2450 | 2498 | 2618 | 2936 | 3015 | 3015
10 | 2898 | 2898 | 3088 | 3015 | 2936 | 2618 | 2450 | 2498 | 2618 | 2936 | 3015 | 3015
11 | 2898 | 2898 | 3015 | 2982 | 2825 | 2450 | 2300 | 2300 | 2498 | 2825 | 2982 | 2982
12 | 2898 | 2898 | 3015 | 2982 | 2825 | 2450 | 2300 | 2300 | 2498 | 2825 | 2982 | 2982
13 | 2898 | 2898 | 3015 | 2982 | 2825 | 2450 | 2300 | 2300 | 2498 | 2825 | 2982 | 2982
14 | 2898 | 2898 | 3015 | 2982 | 2825 | 2450 | 2300 | 2300 | 2498 | 2825 | 2982 | 2982
15 | 2898 | 2936 | 2982 | 2936 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2936 | 2982
16 | 2898 | 2936 | 2982 | 2936 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2936 | 2982
17 | 2898 | 2936 | 2982 | 2936 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2936 | 2982
18 | 2898 | 2936 | 2982 | 2936 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2936 | 2982
19 | 2898 | 2936 | 2982 | 2936 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2982 | 2982
20 | 2898 | 2936 | 2982 | 2936 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2982 | 2982
21 | 2898 | 2936 | 2982 | 2936 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2982 | 2982
22 | 2898 | 2936 | 2982 | 2936 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2982 | 2982
23 | 2982 | 3015 | 3178 | 3088 | 2982 | 2668 | 2498 | 2498 | 2732 | 2982 | 3178 | 3128
24 | 2982 | 3015 | 3178 | 3088 | 2982 | 2668 | 2498 | 2498 | 2732 | 2982 | 3178 | 3128
Total | 70224 | 70792 | 73692 | 72340 | 69432 | 64644 | 61544 | 61736 | 65092 | 69432 | 73084 | 72708
These preliminary 2022 quantities above are based on the 2022 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW, the minimum RRS-PFR limit of 1240 MW and a floor of 2300 MW across all hours. Note that, NERC’s preliminary 2022 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows a reduction in ERCOT’s IFRO. This is primarily because of an update in the IFRO methodology that as approved as a part of the Project 2017-01, Modifications to BAL-003. As a result of this ERCOT expects that the minimum RRS-PFR limit for 2022 will change to align with ERCOT's new IFRO.

## 2022_RRS_Details
These preliminary 2022 quantities above are based on the 2022 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW, the minimum RRS-PFR limit of 1240 MW and a floor of 2300 MW across all hours. Note that, NERC’s preliminary 2022 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows a reduction in ERCOT’s IFRO. This is primarily because of an update in the IFRO methodology that as approved as a part of the Project 2017-01, Modifications to BAL-003. As a result of this ERCOT expects that the minimum RRS-PFR limit for 2022 will change to align with ERCOT's new IFRO.
2022-01-01 | [5 empty] | 2022-02-01 | [5 empty] | 2022-03-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 1 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 1 | 3178 | 1271 | 1907 | 2.06 | 60.01%
2 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 2 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 2 | 3178 | 1271 | 1907 | 2.06 | 60.01%
3 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 3 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 3 | 3178 | 1271 | 1907 | 2.06 | 60.01%
4 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 4 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 4 | 3178 | 1271 | 1907 | 2.06 | 60.01%
5 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 5 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 5 | 3178 | 1271 | 1907 | 2.06 | 60.01%
6 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 6 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 6 | 3178 | 1271 | 1907 | 2.06 | 60.01%
7 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 7 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 7 | 3088 | 1240 | 1848 | 1.83 | 59.84%
8 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 8 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 8 | 3088 | 1240 | 1848 | 1.83 | 59.84%
9 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 9 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 9 | 3088 | 1240 | 1848 | 1.83 | 59.84%
10 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 10 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 10 | 3088 | 1240 | 1848 | 1.83 | 59.84%
11 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 11 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 11 | 3015 | 1240 | 1775 | 1.74 | 58.87%
12 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 12 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 12 | 3015 | 1240 | 1775 | 1.74 | 58.87%
13 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 13 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 13 | 3015 | 1240 | 1775 | 1.74 | 58.87%
14 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 14 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 14 | 3015 | 1240 | 1775 | 1.74 | 58.87%
15 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 15 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 15 | 2982 | 1240 | 1742 | 1.65 | 58.42%
16 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 16 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 16 | 2982 | 1240 | 1742 | 1.65 | 58.42%
17 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 17 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 17 | 2982 | 1240 | 1742 | 1.65 | 58.42%
18 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 18 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 18 | 2982 | 1240 | 1742 | 1.65 | 58.42%
19 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 19 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 19 | 2982 | 1240 | 1742 | 1.65 | 58.42%
20 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 20 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 20 | 2982 | 1240 | 1742 | 1.65 | 58.42%
21 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 21 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 21 | 2982 | 1240 | 1742 | 1.65 | 58.42%
22 | 2898 | 1240 | 1658 | 1.51 | 57.21% | 22 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 22 | 2982 | 1240 | 1742 | 1.65 | 58.42%
23 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 23 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 23 | 3178 | 1271 | 1907 | 2.06 | 60.01%
24 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 24 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 24 | 3178 | 1271 | 1907 | 2.06 | 60.01%
2022-04-01 | [5 empty] | 2022-05-01 | [5 empty] | 2022-06-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3088 | 1240 | 1848 | 1.83 | 59.84% | 1 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 1 | 2668 | 1240 | 1428 | 1.33 | 53.52%
2 | 3088 | 1240 | 1848 | 1.83 | 59.84% | 2 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 2 | 2668 | 1240 | 1428 | 1.33 | 53.52%
3 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 3 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 3 | 2825 | 1240 | 1585 | 1.44 | 56.11%
4 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 4 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 4 | 2825 | 1240 | 1585 | 1.44 | 56.11%
5 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 5 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 5 | 2825 | 1240 | 1585 | 1.44 | 56.11%
6 | 3128 | 1251 | 1877 | 1.94 | 60.01% | 6 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 6 | 2825 | 1240 | 1585 | 1.44 | 56.11%
7 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 7 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 7 | 2618 | 1240 | 1378 | 1.28 | 52.64%
8 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 8 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 8 | 2618 | 1240 | 1378 | 1.28 | 52.64%
9 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 9 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 9 | 2618 | 1240 | 1378 | 1.28 | 52.64%
10 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 10 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 10 | 2618 | 1240 | 1378 | 1.28 | 52.64%
11 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 11 | 2825 | 1240 | 1585 | 1.44 | 56.11% | 11 | 2450 | 1240 | 1210 | 1.12 | 49.39%
12 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 12 | 2825 | 1240 | 1585 | 1.44 | 56.11% | 12 | 2450 | 1240 | 1210 | 1.12 | 49.39%
13 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 13 | 2825 | 1240 | 1585 | 1.44 | 56.11% | 13 | 2450 | 1240 | 1210 | 1.12 | 49.39%
14 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 14 | 2825 | 1240 | 1585 | 1.44 | 56.11% | 14 | 2450 | 1240 | 1210 | 1.12 | 49.39%
15 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 15 | 2800 | 1240 | 1560 | 1.39 | 55.71% | 15 | 2800 | 1240 | 1560 | 1.04 | 55.71%
16 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 16 | 2800 | 1240 | 1560 | 1.39 | 55.71% | 16 | 2800 | 1240 | 1560 | 1.04 | 55.71%
17 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 17 | 2800 | 1240 | 1560 | 1.39 | 55.71% | 17 | 2800 | 1240 | 1560 | 1.04 | 55.71%
18 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 18 | 2800 | 1240 | 1560 | 1.39 | 55.71% | 18 | 2800 | 1240 | 1560 | 1.04 | 55.71%
19 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 19 | 2800 | 1240 | 1560 | 1.39 | 55.71% | 19 | 2800 | 1240 | 1560 | 1.12 | 55.71%
20 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 20 | 2800 | 1240 | 1560 | 1.39 | 55.71% | 20 | 2800 | 1240 | 1560 | 1.12 | 55.71%
21 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 21 | 2800 | 1240 | 1560 | 1.39 | 55.71% | 21 | 2800 | 1240 | 1560 | 1.12 | 55.71%
22 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 22 | 2800 | 1240 | 1492 | 1.39 | 53.29% | 22 | 2800 | 1240 | 1210 | 1.12 | 43.21%
23 | 3088 | 1240 | 1848 | 1.83 | 59.84% | 23 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 23 | 2668 | 1240 | 1428 | 1.33 | 53.52%
24 | 3088 | 1240 | 1848 | 1.83 | 59.84% | 24 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 24 | 2668 | 1240 | 1428 | 1.33 | 53.52%
2222-07-01 | [5 empty] | 2222-08-01 | [5 empty] | 2222-09-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 1 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 1 | 2732 | 1240 | 1492 | 1.39 | 54.61%
2 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 2 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 2 | 2732 | 1240 | 1492 | 1.39 | 54.61%
3 | 2538 | 1240 | 1298 | 1.19 | 51.14% | 3 | 2538 | 1240 | 1298 | 1.19 | 51.14% | 3 | 2825 | 1240 | 1585 | 1.44 | 56.11%
4 | 2538 | 1240 | 1298 | 1.19 | 51.14% | 4 | 2538 | 1240 | 1298 | 1.19 | 51.14% | 4 | 2825 | 1240 | 1585 | 1.44 | 56.11%
5 | 2538 | 1240 | 1298 | 1.19 | 51.14% | 5 | 2538 | 1240 | 1298 | 1.19 | 51.14% | 5 | 2825 | 1240 | 1585 | 1.44 | 56.11%
6 | 2538 | 1240 | 1298 | 1.19 | 51.14% | 6 | 2538 | 1240 | 1298 | 1.19 | 51.14% | 6 | 2825 | 1240 | 1585 | 1.44 | 56.11%
7 | 2450 | 1240 | 1210 | 1.12 | 49.39% | 7 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 7 | 2618 | 1240 | 1378 | 1.28 | 52.64%
8 | 2450 | 1240 | 1210 | 1.12 | 49.39% | 8 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 8 | 2618 | 1240 | 1378 | 1.28 | 52.64%
9 | 2450 | 1240 | 1210 | 1.12 | 49.39% | 9 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 9 | 2618 | 1240 | 1378 | 1.28 | 52.64%
10 | 2450 | 1240 | 1210 | 1.12 | 49.39% | 10 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 10 | 2618 | 1240 | 1378 | 1.28 | 52.64%
11 | 2300 | 1240 | 1060 | 1 | 46.09% | 11 | 2300 | 1240 | 1060 | 1 | 46.09% | 11 | 2498 | 1240 | 1258 | 1.15 | 50.36%
12 | 2300 | 1240 | 1060 | 1 | 46.09% | 12 | 2300 | 1240 | 1060 | 1 | 46.09% | 12 | 2498 | 1240 | 1258 | 1.15 | 50.36%
13 | 2300 | 1240 | 1060 | 1 | 46.09% | 13 | 2300 | 1240 | 1060 | 1 | 46.09% | 13 | 2498 | 1240 | 1258 | 1.15 | 50.36%
14 | 2300 | 1240 | 1060 | 1 | 46.09% | 14 | 2300 | 1240 | 1060 | 1 | 46.09% | 14 | 2498 | 1240 | 1258 | 1.15 | 50.36%
15 | 2800 | 1240 | 1560 | 1 | 55.71% | 15 | 2800 | 1240 | 1560 | 1 | 55.71% | 15 | 2800 | 1240 | 1560 | 1.12 | 55.71%
16 | 2800 | 1240 | 1560 | 1 | 55.71% | 16 | 2800 | 1240 | 1560 | 1 | 55.71% | 16 | 2800 | 1240 | 1560 | 1.12 | 55.71%
17 | 2800 | 1240 | 1560 | 1 | 55.71% | 17 | 2800 | 1240 | 1560 | 1 | 55.71% | 17 | 2800 | 1240 | 1560 | 1.12 | 55.71%
18 | 2800 | 1240 | 1560 | 1 | 55.71% | 18 | 2800 | 1240 | 1560 | 1 | 55.71% | 18 | 2800 | 1240 | 1560 | 1.12 | 55.71%
19 | 2800 | 1240 | 1560 | 1 | 55.71% | 19 | 2800 | 1240 | 1560 | 1 | 55.71% | 19 | 2800 | 1240 | 1560 | 1.12 | 55.71%
20 | 2800 | 1240 | 1560 | 1 | 55.71% | 20 | 2800 | 1240 | 1560 | 1 | 55.71% | 20 | 2800 | 1240 | 1560 | 1.12 | 55.71%
21 | 2800 | 1240 | 1560 | 1 | 55.71% | 21 | 2800 | 1240 | 1560 | 1 | 55.71% | 21 | 2800 | 1240 | 1560 | 1.12 | 55.71%
22 | 2800 | 1240 | 1060 | 1 | 37.86% | 22 | 2800 | 1240 | 1060 | 1 | 37.86% | 22 | 2800 | 1240 | 1210 | 1.12 | 43.21%
23 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 23 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 23 | 2732 | 1240 | 1492 | 1.39 | 54.61%
24 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 24 | 2498 | 1240 | 1258 | 1.15 | 50.36% | 24 | 2732 | 1240 | 1492 | 1.39 | 54.61%
2222-10-01 | [5 empty] | 2222-11-01 | [5 empty] | 2222-12-01
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 1 | 3178 | 1271 | 1907 | 2.06 | 60.01% | 1 | 3128 | 1251 | 1877 | 1.94 | 60.01%
2 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 2 | 3178 | 1271 | 1907 | 2.06 | 60.01% | 2 | 3128 | 1251 | 1877 | 1.94 | 60.01%
3 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 3 | 3178 | 1271 | 1907 | 2.06 | 60.01% | 3 | 3088 | 1240 | 1848 | 1.83 | 59.84%
4 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 4 | 3178 | 1271 | 1907 | 2.06 | 60.01% | 4 | 3088 | 1240 | 1848 | 1.83 | 59.84%
5 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 5 | 3178 | 1271 | 1907 | 2.06 | 60.01% | 5 | 3088 | 1240 | 1848 | 1.83 | 59.84%
6 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 6 | 3178 | 1271 | 1907 | 2.06 | 60.01% | 6 | 3088 | 1240 | 1848 | 1.83 | 59.84%
7 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 7 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 7 | 3015 | 1240 | 1775 | 1.74 | 58.87%
8 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 8 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 8 | 3015 | 1240 | 1775 | 1.74 | 58.87%
9 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 9 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 9 | 3015 | 1240 | 1775 | 1.74 | 58.87%
10 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 10 | 3015 | 1240 | 1775 | 1.74 | 58.87% | 10 | 3015 | 1240 | 1775 | 1.74 | 58.87%
11 | 2825 | 1240 | 1585 | 1.44 | 56.11% | 11 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 11 | 2982 | 1240 | 1742 | 1.65 | 58.42%
12 | 2825 | 1240 | 1585 | 1.44 | 56.11% | 12 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 12 | 2982 | 1240 | 1742 | 1.65 | 58.42%
13 | 2825 | 1240 | 1585 | 1.44 | 56.11% | 13 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 13 | 2982 | 1240 | 1742 | 1.65 | 58.42%
14 | 2825 | 1240 | 1585 | 1.44 | 56.11% | 14 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 14 | 2982 | 1240 | 1742 | 1.65 | 58.42%
15 | 2800 | 1240 | 1560 | 1.12 | 55.71% | 15 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 15 | 2982 | 1240 | 1742 | 1.65 | 58.42%
16 | 2800 | 1240 | 1560 | 1.12 | 55.71% | 16 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 16 | 2982 | 1240 | 1742 | 1.65 | 58.42%
17 | 2800 | 1240 | 1560 | 1.12 | 55.71% | 17 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 17 | 2982 | 1240 | 1742 | 1.65 | 58.42%
18 | 2800 | 1240 | 1560 | 1.12 | 55.71% | 18 | 2936 | 1240 | 1696 | 1.58 | 57.77% | 18 | 2982 | 1240 | 1742 | 1.65 | 58.42%
19 | 2800 | 1240 | 1560 | 1.12 | 55.71% | 19 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 19 | 2982 | 1240 | 1742 | 1.65 | 58.42%
20 | 2800 | 1240 | 1560 | 1.12 | 55.71% | 20 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 20 | 2982 | 1240 | 1742 | 1.65 | 58.42%
21 | 2800 | 1240 | 1560 | 1.12 | 55.71% | 21 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 21 | 2982 | 1240 | 1742 | 1.65 | 58.42%
22 | 2800 | 1240 | 1210 | 1.12 | 43.21% | 22 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 22 | 2982 | 1240 | 1742 | 1.65 | 58.42%
23 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 23 | 3178 | 1271 | 1907 | 2.06 | 60.01% | 23 | 3128 | 1251 | 1877 | 1.94 | 60.01%
24 | 2982 | 1240 | 1742 | 1.65 | 58.42% | 24 | 3178 | 1271 | 1907 | 2.06 | 60.01% | 24 | 3128 | 1251 | 1877 | 1.94 | 60.01%

## 2023_RRS
*Note that all quantities listed in this table are preliminary and final 2023 AS quantities will be posted on ercot.com and MIS by Dec 20, 2022. 2023 Jan thru Oct quantities have been computed using 2021 and 2022 data. 2023 Nov and Dec quantities have been computed using 2020 and 2021 data.
2023 RRS (Floor = 2800 MW for peak hours ¦ Floor = 2300 MW for remaining hours, new minimum RRS-PFR limit =1390 MW)
HE | Jan | Feb | Mar | Apr | May | Jun | July | Aug | Sep | Oct | Nov* | Dec*
1 | 3041 | 3079 | 3335 | 3195 | 3041 | 2651 | 2517 | 2517 | 2705 | 3079 | 3239 | 3195
2 | 3041 | 3079 | 3335 | 3195 | 3041 | 2651 | 2517 | 2517 | 2705 | 3079 | 3239 | 3195
3 | 2991 | 3041 | 3335 | 3239 | 3041 | 2774 | 2562 | 2600 | 2774 | 3156 | 3239 | 3195
4 | 2991 | 3041 | 3335 | 3239 | 3041 | 2774 | 2562 | 2600 | 2774 | 3156 | 3239 | 3195
5 | 2991 | 3041 | 3335 | 3239 | 3041 | 2774 | 2562 | 2600 | 2774 | 3156 | 3239 | 3195
6 | 2991 | 3041 | 3335 | 3239 | 3041 | 2774 | 2562 | 2600 | 2774 | 3156 | 3239 | 3195
7 | 2871 | 2991 | 3239 | 3156 | 2949 | 2651 | 2517 | 2517 | 2651 | 2991 | 3079 | 3079
8 | 2871 | 2991 | 3239 | 3156 | 2949 | 2651 | 2517 | 2517 | 2651 | 2991 | 3079 | 3079
9 | 2871 | 2991 | 3239 | 3156 | 2949 | 2651 | 2517 | 2517 | 2651 | 2991 | 3079 | 3079
10 | 2871 | 2991 | 3239 | 3156 | 2949 | 2651 | 2517 | 2517 | 2651 | 2991 | 3079 | 3079
11 | 2949 | 3041 | 3239 | 3041 | 2774 | 2381 | 2300 | 2300 | 2427 | 2871 | 3041 | 3041
12 | 2949 | 3041 | 3239 | 3041 | 2774 | 2381 | 2300 | 2300 | 2427 | 2871 | 3041 | 3041
13 | 2949 | 3041 | 3239 | 3041 | 2774 | 2381 | 2300 | 2300 | 2427 | 2871 | 3041 | 3041
14 | 2949 | 3041 | 3239 | 3041 | 2774 | 2381 | 2300 | 2300 | 2427 | 2871 | 3041 | 3041
15 | 2991 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2991
16 | 2991 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2991
17 | 2991 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2991
18 | 2991 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2991 | 2991
19 | 2949 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 3041 | 2991
20 | 2949 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 3041 | 2991
21 | 2949 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 3041 | 2991
22 | 2949 | 2991 | 3195 | 2991 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 3041 | 2991
23 | 3041 | 3079 | 3335 | 3195 | 3041 | 2651 | 2517 | 2517 | 2705 | 3079 | 3239 | 3195
24 | 3041 | 3079 | 3335 | 3195 | 3041 | 2651 | 2517 | 2517 | 2705 | 3079 | 3239 | 3195
Total | 71168 | 72536 | 78152 | 74452 | 69620 | 64228 | 61984 | 62136 | 64628 | 70788 | 74520 | 73968
These preliminary 2023 quantities above are based on the 2023 RRS table that was built using Resource Contingency Criteria (RCC) of 2805 MW, the minimum RRS-PFR limit of 1390 MW and a floor of 2300 MW across all hours. Note that, NERC’s preliminary 2024 BAL-003 Interconnection Frequency Response Obligation (IFRO) assessment for ERCOT shows an increase in ERCOT’s IFRO. As a result of this ERCOT expects that the minimum RRS-PFR limit for 2023 will change to align with ERCOT's new IFRO.

## 2023_RRS_Details
*Note that all quantities listed in this table are preliminary and final 2023 AS quantities will be posted on ercot.com and MIS by Dec 20, 2022. 2023 Jan thru Oct quantities have been computed using 2021 and 2022 data. 2023 Nov and Dec quantities have been computed using 2020 and 2021 data.
Jan-23 | [5 empty] | Feb-23 | [5 empty] | Mar-23
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 1 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 1 | 3335 | 1390 | 1945 | 2.35 | 58.32%
2 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 2 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 2 | 3335 | 1390 | 1945 | 2.35 | 58.32%
3 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 3 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 3 | 3335 | 1390 | 1945 | 2.35 | 58.32%
4 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 4 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 4 | 3335 | 1390 | 1945 | 2.35 | 58.32%
5 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 5 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 5 | 3335 | 1390 | 1945 | 2.35 | 58.32%
6 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 6 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 6 | 3335 | 1390 | 1945 | 2.35 | 58.32%
7 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 7 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 7 | 3239 | 1390 | 1849 | 2.06 | 57.09%
8 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 8 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 8 | 3239 | 1390 | 1849 | 2.06 | 57.09%
9 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 9 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 9 | 3239 | 1390 | 1849 | 2.06 | 57.09%
10 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 10 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 10 | 3239 | 1390 | 1849 | 2.06 | 57.09%
11 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 11 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 11 | 3239 | 1390 | 1849 | 2.06 | 57.09%
12 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 12 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 12 | 3239 | 1390 | 1849 | 2.06 | 57.09%
13 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 13 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 13 | 3239 | 1390 | 1849 | 2.06 | 57.09%
14 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 14 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 14 | 3239 | 1390 | 1849 | 2.06 | 57.09%
15 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 15 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 15 | 3195 | 1390 | 1805 | 1.94 | 56.49%
16 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 16 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 16 | 3195 | 1390 | 1805 | 1.94 | 56.49%
17 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 17 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 17 | 3195 | 1390 | 1805 | 1.94 | 56.49%
18 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 18 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 18 | 3195 | 1390 | 1805 | 1.94 | 56.49%
19 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 19 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 19 | 3195 | 1390 | 1805 | 1.94 | 56.49%
20 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 20 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 20 | 3195 | 1390 | 1805 | 1.94 | 56.49%
21 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 21 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 21 | 3195 | 1390 | 1805 | 1.94 | 56.49%
22 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 22 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 22 | 3195 | 1390 | 1805 | 1.94 | 56.49%
23 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 23 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 23 | 3335 | 1390 | 1945 | 2.35 | 58.32%
24 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 24 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 24 | 3335 | 1390 | 1945 | 2.35 | 58.32%
Apr-23 | [5 empty] | May-23 | [5 empty] | Jun-23
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 1 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 1 | 2651 | 1390 | 1261 | 1.28 | 47.57%
2 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 2 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 2 | 2651 | 1390 | 1261 | 1.28 | 47.57%
3 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 3 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 3 | 2774 | 1390 | 1384 | 1.39 | 49.89%
4 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 4 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 4 | 2774 | 1390 | 1384 | 1.39 | 49.89%
5 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 5 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 5 | 2774 | 1390 | 1384 | 1.39 | 49.89%
6 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 6 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 6 | 2774 | 1390 | 1384 | 1.39 | 49.89%
7 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 7 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 7 | 2651 | 1390 | 1261 | 1.28 | 47.57%
8 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 8 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 8 | 2651 | 1390 | 1261 | 1.28 | 47.57%
9 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 9 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 9 | 2651 | 1390 | 1261 | 1.28 | 47.57%
10 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 10 | 2949 | 1390 | 1559 | 1.51 | 52.87% | 10 | 2651 | 1390 | 1261 | 1.28 | 47.57%
11 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 11 | 2774 | 1390 | 1384 | 1.39 | 49.89% | 11 | 2381 | 1390 | 991 | 1.04 | 41.62%
12 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 12 | 2774 | 1390 | 1384 | 1.39 | 49.89% | 12 | 2381 | 1390 | 991 | 1.04 | 41.62%
13 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 13 | 2774 | 1390 | 1384 | 1.39 | 49.89% | 13 | 2381 | 1390 | 991 | 1.04 | 41.62%
14 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 14 | 2774 | 1390 | 1384 | 1.39 | 49.89% | 14 | 2381 | 1390 | 991 | 1.04 | 41.62%
15 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 15 | 2705 | 1390 | 1315 | 1.33 | 48.61% | 15 | 2344 | 1390 | 954 | 1.01 | 40.7%
16 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 16 | 2705 | 1390 | 1315 | 1.33 | 48.61% | 16 | 2344 | 1390 | 954 | 1.01 | 40.7%
17 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 17 | 2705 | 1390 | 1315 | 1.33 | 48.61% | 17 | 2344 | 1390 | 954 | 1.01 | 40.7%
18 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 18 | 2705 | 1390 | 1315 | 1.33 | 48.61% | 18 | 2344 | 1390 | 954 | 1.01 | 40.7%
19 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 19 | 2705 | 1390 | 1315 | 1.33 | 48.61% | 19 | 2381 | 1390 | 991 | 1.04 | 41.62%
20 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 20 | 2705 | 1390 | 1315 | 1.33 | 48.61% | 20 | 2381 | 1390 | 991 | 1.04 | 41.62%
21 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 21 | 2705 | 1390 | 1315 | 1.33 | 48.61% | 21 | 2381 | 1390 | 991 | 1.04 | 41.62%
22 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 22 | 2705 | 1390 | 1315 | 1.33 | 48.61% | 22 | 2381 | 1390 | 991 | 1.04 | 41.62%
23 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 23 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 23 | 2651 | 1390 | 1261 | 1.28 | 47.57%
24 | 3195 | 1390 | 1805 | 1.94 | 56.49% | 24 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 24 | 2651 | 1390 | 1261 | 1.28 | 47.57%
Jul-23 | [5 empty] | Aug-23 | [5 empty] | Sep-23
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 1 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 1 | 2705 | 1390 | 1315 | 1.33 | 48.61%
2 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 2 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 2 | 2705 | 1390 | 1315 | 1.33 | 48.61%
3 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 3 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 3 | 2774 | 1390 | 1384 | 1.39 | 49.89%
4 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 4 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 4 | 2774 | 1390 | 1384 | 1.39 | 49.89%
5 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 5 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 5 | 2774 | 1390 | 1384 | 1.39 | 49.89%
6 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 6 | 2562 | 1390 | 1172 | 1.19 | 45.75% | 6 | 2774 | 1390 | 1384 | 1.39 | 49.89%
7 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 7 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 7 | 2651 | 1390 | 1261 | 1.28 | 47.57%
8 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 8 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 8 | 2651 | 1390 | 1261 | 1.28 | 47.57%
9 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 9 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 9 | 2651 | 1390 | 1261 | 1.28 | 47.57%
10 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 10 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 10 | 2651 | 1390 | 1261 | 1.28 | 47.57%
11 | 2300 | 1390 | 910 | 1 | 39.57% | 11 | 2300 | 1390 | 910 | 1 | 39.57% | 11 | 2427 | 1390 | 1037 | 1.08 | 42.73%
12 | 2300 | 1390 | 910 | 1 | 39.57% | 12 | 2300 | 1390 | 910 | 1 | 39.57% | 12 | 2427 | 1390 | 1037 | 1.08 | 42.73%
13 | 2300 | 1390 | 910 | 1 | 39.57% | 13 | 2300 | 1390 | 910 | 1 | 39.57% | 13 | 2427 | 1390 | 1037 | 1.08 | 42.73%
14 | 2300 | 1390 | 910 | 1 | 39.57% | 14 | 2300 | 1390 | 910 | 1 | 39.57% | 14 | 2427 | 1390 | 1037 | 1.08 | 42.73%
15 | 2300 | 1390 | 910 | 1 | 39.57% | 15 | 2300 | 1390 | 910 | 1 | 39.57% | 15 | 2381 | 1390 | 991 | 1.04 | 41.62%
16 | 2300 | 1390 | 910 | 1 | 39.57% | 16 | 2300 | 1390 | 910 | 1 | 39.57% | 16 | 2381 | 1390 | 991 | 1.04 | 41.62%
17 | 2300 | 1390 | 910 | 1 | 39.57% | 17 | 2300 | 1390 | 910 | 1 | 39.57% | 17 | 2381 | 1390 | 991 | 1.04 | 41.62%
18 | 2300 | 1390 | 910 | 1 | 39.57% | 18 | 2300 | 1390 | 910 | 1 | 39.57% | 18 | 2381 | 1390 | 991 | 1.04 | 41.62%
19 | 2300 | 1390 | 910 | 1 | 39.57% | 19 | 2300 | 1390 | 910 | 1 | 39.57% | 19 | 2381 | 1390 | 991 | 1.04 | 41.62%
20 | 2300 | 1390 | 910 | 1 | 39.57% | 20 | 2300 | 1390 | 910 | 1 | 39.57% | 20 | 2381 | 1390 | 991 | 1.04 | 41.62%
21 | 2300 | 1390 | 910 | 1 | 39.57% | 21 | 2300 | 1390 | 910 | 1 | 39.57% | 21 | 2381 | 1390 | 991 | 1.04 | 41.62%
22 | 2300 | 1390 | 910 | 1 | 39.57% | 22 | 2300 | 1390 | 910 | 1 | 39.57% | 22 | 2381 | 1390 | 991 | 1.04 | 41.62%
23 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 23 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 23 | 2705 | 1390 | 1315 | 1.33 | 48.61%
24 | 2517 | 1390 | 1127 | 1.15 | 44.78% | 24 | 2466 | 1390 | 1076 | 1.12 | 43.63% | 24 | 2705 | 1390 | 1315 | 1.33 | 48.61%
Oct-23 | [5 empty] | Nov-22* | [5 empty] | Dec-22*
HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs | HE | Total RRS MW | PFRS | LRs | Equivalency Ratio | %RRS from LRs
1 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 1 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 1 | 3195 | 1390 | 1805 | 1.94 | 56.49%
2 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 2 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 2 | 3195 | 1390 | 1805 | 1.94 | 56.49%
3 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 3 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 3 | 3195 | 1390 | 1805 | 1.94 | 56.49%
4 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 4 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 4 | 3195 | 1390 | 1805 | 1.94 | 56.49%
5 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 5 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 5 | 3195 | 1390 | 1805 | 1.94 | 56.49%
6 | 3156 | 1390 | 1766 | 1.83 | 55.96% | 6 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 6 | 3195 | 1390 | 1805 | 1.94 | 56.49%
7 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 7 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 7 | 3079 | 1390 | 1689 | 1.74 | 54.86%
8 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 8 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 8 | 3079 | 1390 | 1689 | 1.74 | 54.86%
9 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 9 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 9 | 3079 | 1390 | 1689 | 1.74 | 54.86%
10 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 10 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 10 | 3079 | 1390 | 1689 | 1.74 | 54.86%
11 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 11 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 11 | 3041 | 1390 | 1651 | 1.65 | 54.29%
12 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 12 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 12 | 3041 | 1390 | 1651 | 1.65 | 54.29%
13 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 13 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 13 | 3041 | 1390 | 1651 | 1.65 | 54.29%
14 | 2871 | 1390 | 1481 | 1.44 | 51.58% | 14 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 14 | 3041 | 1390 | 1651 | 1.65 | 54.29%
15 | 2800 | 1390 | 1410 | 1.39 | 50.36% | 15 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 15 | 2991 | 1390 | 1601 | 1.58 | 53.53%
16 | 2800 | 1390 | 1410 | 1.39 | 50.36% | 16 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 16 | 2991 | 1390 | 1601 | 1.58 | 53.53%
17 | 2800 | 1390 | 1410 | 1.39 | 50.36% | 17 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 17 | 2991 | 1390 | 1601 | 1.58 | 53.53%
18 | 2800 | 1390 | 1410 | 1.39 | 50.36% | 18 | 2991 | 1390 | 1601 | 1.58 | 53.53% | 18 | 2991 | 1390 | 1601 | 1.58 | 53.53%
19 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 19 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 19 | 2991 | 1390 | 1601 | 1.58 | 53.53%
20 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 20 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 20 | 2991 | 1390 | 1601 | 1.58 | 53.53%
21 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 21 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 21 | 2991 | 1390 | 1601 | 1.58 | 53.53%
22 | 2800 | 1390 | 1410 | 1.33 | 50.36% | 22 | 3041 | 1390 | 1651 | 1.65 | 54.29% | 22 | 2991 | 1390 | 1601 | 1.58 | 53.53%
23 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 23 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 23 | 3195 | 1390 | 1805 | 1.94 | 56.49%
24 | 3079 | 1390 | 1689 | 1.74 | 54.86% | 24 | 3239 | 1390 | 1849 | 2.06 | 57.09% | 24 | 3195 | 1390 | 1805 | 1.94 | 56.49%

## Charts
Month | Date | Group | HE | Type | 2022 RRS | 2023 RRS | Delta-1 | Month | Dec |  |  | Responsive Reserve Requirement Comparison for December
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2982 | 3041 | 59 | Type | RRS |  |  | Range: 2991 MW - 3195 MW; Avg: 3082 MW (53 MW increase from prev year)
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2982 | 3041 | 59 | [8 empty] | Max of 2022 RRS | Column Labels
Jan | 2018-01-01 | b. HE3-6 | 3 | RRS | 2982 | 2991 | 9 | Row Labels | 2022 RRS | 2023 RRS |  |  | min | 2991 |  | Row Labels | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | (blank) | Grand Total
Jan | 2018-01-01 | b. HE3-6 | 4 | RRS | 2982 | 2991 | 9 | a. HE1-2 & HE23-24 | 3128 | 3195 |  |  | max | 3195 |  | Jan | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2982 | 2982 |  | 2982
Jan | 2018-01-01 | b. HE3-6 | 5 | RRS | 2982 | 2991 | 9 | b. HE3-6 | 3088 | 3195 |  |  | avg | 3082 |  | Feb | 3015 | 3015 | 3015 | 3015 | 3015 | 3015 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2898 | 2936 | 2936 | 2936 | 2936 | 2936 | 2936 | 2936 | 2936 | 3015 | 3015 |  | 3015
Jan | 2018-01-01 | b. HE3-6 | 6 | RRS | 2982 | 2991 | 9 | c. HE7-10 | 3015 | 3079 |  |  | Change | 53 |  | Mar | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3088 | 3088 | 3088 | 3088 | 3015 | 3015 | 3015 | 3015 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 3178 | 3178 |  | 3178
Jan | 2018-01-01 | c. HE7-10 | 7 | RRS | 2898 | 2871 | -27 | d. HE11-14 | 2982 | 3041 | [5 empty] | Apr | 3088 | 3088 | 3128 | 3128 | 3128 | 3128 | 3015 | 3015 | 3015 | 3015 | 2982 | 2982 | 2982 | 2982 | 2936 | 2936 | 2936 | 2936 | 2936 | 2936 | 2936 | 2936 |  |  |  | 3128
Jan | 2018-01-01 | c. HE7-10 | 8 | RRS | 2898 | 2871 | -27 | e. HE15-18 | 2982 | 2991 | [5 empty] | May | 2982 | 2982 | 3015 | 3015 | 3015 | 3015 | 2936 | 2936 | 2936 | 2936 | 2825 | 2825 | 2825 | 2825 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 3088 | 3088 |  | 3088
Jan | 2018-01-01 | c. HE7-10 | 9 | RRS | 2898 | 2871 | -27 | f. HE19-22 | 2982 | 2991 | [5 empty] | Jun | 2668 | 2668 | 2825 | 2825 | 2825 | 2825 | 2618 | 2618 | 2618 | 2618 | 2450 | 2450 | 2450 | 2450 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2668 | 2668 |  | 2825
Jan | 2018-01-01 | c. HE7-10 | 10 | RRS | 2898 | 2871 | -27 | [8 empty] | Jul | 2498 | 2498 | 2538 | 2538 | 2538 | 2538 | 2450 | 2450 | 2450 | 2450 | 2300 | 2300 | 2300 | 2300 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2498 | 2498 |  | 2800
Jan | 2018-01-01 | d. HE11-14 | 11 | RRS | 2898 | 2949 | 51 | [8 empty] | Aug | 2498 | 2498 | 2538 | 2538 | 2538 | 2538 | 2498 | 2498 | 2498 | 2498 | 2300 | 2300 | 2300 | 2300 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2498 | 2498 |  | 2800
Jan | 2018-01-01 | d. HE11-14 | 12 | RRS | 2898 | 2949 | 51 | [8 empty] | Sep | 2732 | 2732 | 2825 | 2825 | 2825 | 2825 | 2618 | 2618 | 2618 | 2618 | 2498 | 2498 | 2498 | 2498 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2732 | 2732 |  | 2825
Jan | 2018-01-01 | d. HE11-14 | 13 | RRS | 2898 | 2949 | 51 | [8 empty] | Oct | 2982 | 2982 | 3015 | 3015 | 3015 | 3015 | 2936 | 2936 | 2936 | 2936 | 2825 | 2825 | 2825 | 2825 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2800 | 2982 | 2982 |  | 3015
Jan | 2018-01-01 | d. HE11-14 | 14 | RRS | 2898 | 2949 | 51 | [8 empty] | Nov | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3015 | 3015 | 3015 | 3015 | 2982 | 2982 | 2982 | 2982 | 2936 | 2936 | 2936 | 2936 | 2982 | 2982 | 2982 | 2982 | 3178 | 3178 |  | 3178
Jan | 2018-01-01 | e. HE15-18 | 15 | RRS | 2898 | 2991 | 93 | [8 empty] | Dec | 3128 | 3128 | 3088 | 3088 | 3088 | 3088 | 3015 | 3015 | 3015 | 3015 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 3128 | 3128 |  | 3128
Jan | 2018-01-01 | e. HE15-18 | 16 | RRS | 2898 | 2991 | 93 | [8 empty] | (blank)
Jan | 2018-01-01 | e. HE15-18 | 17 | RRS | 2898 | 2991 | 93 | [8 empty] | Grand Total | 3178 | 3178 | 3178 | 3178 | 3178 | 3178 | 3088 | 3088 | 3088 | 3088 | 3015 | 3015 | 3015 | 3015 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 2982 | 3178 | 3178 |  | 3178
Jan | 2018-01-01 | e. HE15-18 | 18 | RRS | 2898 | 2991 | 93
Jan | 2018-01-01 | f. HE19-22 | 19 | RRS | 2898 | 2949 | 51
Jan | 2018-01-01 | f. HE19-22 | 20 | RRS | 2898 | 2949 | 51
Jan | 2018-01-01 | f. HE19-22 | 21 | RRS | 2898 | 2949 | 51
Jan | 2018-01-01 | f. HE19-22 | 22 | RRS | 2898 | 2949 | 51
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2982 | 3041 | 59
Jan | 2018-01-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2982 | 3041 | 59
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3015 | 3079 | 64
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3015 | 3079 | 64
Feb | 2018-02-01 | b. HE3-6 | 3 | RRS | 3015 | 3041 | 26
Feb | 2018-02-01 | b. HE3-6 | 4 | RRS | 3015 | 3041 | 26
Feb | 2018-02-01 | b. HE3-6 | 5 | RRS | 3015 | 3041 | 26 | Type | RRS |  |  | Hourly Average Responsive Reserve Requirement Comparison
Feb | 2018-02-01 | b. HE3-6 | 6 | RRS | 3015 | 3041 | 26 |  |  |  |  | On avg. 45 MW increase from prev year. Largest increase is in Mar by 186 MW. Largest decrease is in Sep by 19 MW.
Feb | 2018-02-01 | c. HE7-10 | 7 | RRS | 2898 | 2991 | 93 | Row Labels | 2022 RRS | 2023 RRS
Feb | 2018-02-01 | c. HE7-10 | 8 | RRS | 2898 | 2991 | 93 | Jan | 2926 | 2965.3333 | 39.3333 |  | min-change | -19.3333 | Sep
Feb | 2018-02-01 | c. HE7-10 | 9 | RRS | 2898 | 2991 | 93 | Feb | 2949.6667 | 3022.3333 | 72.6667 |  | max-change | 185.8333 | Mar
Feb | 2018-02-01 | c. HE7-10 | 10 | RRS | 2898 | 2991 | 93 | Mar | 3070.5 | 3256.3333 | 185.8333 |  | AVG-CHANGE | 45.4401
Feb | 2018-02-01 | d. HE11-14 | 11 | RRS | 2898 | 3041 | 143 | Apr | 3007.4545 | 3093.7273 | 86.2727
Feb | 2018-02-01 | d. HE11-14 | 12 | RRS | 2898 | 3041 | 143 | May | 2908 | 2923.4615 | 15.4615
Feb | 2018-02-01 | d. HE11-14 | 13 | RRS | 2898 | 3041 | 143 | Jun | 2693.5 | 2676.1667 | -17.3333
Feb | 2018-02-01 | d. HE11-14 | 14 | RRS | 2898 | 3041 | 143 | Jul | 2564.3333 | 2582.6667 | 18.3333
Feb | 2018-02-01 | e. HE15-18 | 15 | RRS | 2936 | 2991 | 55 | Aug | 2572.3333 | 2589 | 16.6667
Feb | 2018-02-01 | e. HE15-18 | 16 | RRS | 2936 | 2991 | 55 | Sep | 2712.1667 | 2692.8333 | -19.3333
Feb | 2018-02-01 | e. HE15-18 | 17 | RRS | 2936 | 2991 | 55 | Oct | 2893 | 2949.5 | 56.5
Feb | 2018-02-01 | e. HE15-18 | 18 | RRS | 2936 | 2991 | 55 | Nov | 3045.1667 | 3105 | 59.8333
Feb | 2018-02-01 | f. HE19-22 | 19 | RRS | 2936 | 2991 | 55 | Dec | 3029.5 | 3082 | 52.5
Feb | 2018-02-01 | f. HE19-22 | 20 | RRS | 2936 | 2991 | 55
Feb | 2018-02-01 | f. HE19-22 | 21 | RRS | 2936 | 2991 | 55
Feb | 2018-02-01 | f. HE19-22 | 22 | RRS | 2936 | 2991 | 55
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3015 | 3079 | 64 | Type | RRS
Feb | 2018-02-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3015 | 3079 | 64
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3178 | 3335 | 157 | Month | Average of Delta-1
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3178 | 3335 | 157 | Jan | 39.3333 | 4
Mar | 2018-03-01 | b. HE3-6 | 3 | RRS | 3178 | 3335 | 157 | Apr | 86.2727 | 2 | p
Mar | 2018-03-01 | b. HE3-6 | 4 | RRS | 3178 | 3335 | 157 | Jul | 18.3333 | 5 | p
Mar | 2018-03-01 | b. HE3-6 | 5 | RRS | 3178 | 3335 | 157 | Oct | 0 | 8
Mar | 2018-03-01 | b. HE3-6 | 6 | RRS | 3178 | 3335 | 157 | Feb | 72.6667 | 3 | p
Mar | 2018-03-01 | c. HE7-10 | 7 | RRS | 3088 | 3239 | 151 | Mar | 185.8333 | 1 | p
Mar | 2018-03-01 | c. HE7-10 | 8 | RRS | 3088 | 3239 | 151 | May | 15.4615 | 7
Mar | 2018-03-01 | c. HE7-10 | 9 | RRS | 3088 | 3239 | 151 | Jun | -17.3333 | 12
Mar | 2018-03-01 | c. HE7-10 | 10 | RRS | 3088 | 3239 | 151 | Aug | 16.6667 | 6
Mar | 2018-03-01 | d. HE11-14 | 11 | RRS | 3015 | 3239 | 224 | Sep | 0 | 8
Mar | 2018-03-01 | d. HE11-14 | 12 | RRS | 3015 | 3239 | 224 | Nov | 0 | 8
Mar | 2018-03-01 | d. HE11-14 | 13 | RRS | 3015 | 3239 | 224 | Dec | 0 | 8
Mar | 2018-03-01 | d. HE11-14 | 14 | RRS | 3015 | 3239 | 224 | Grand Total | 34.2778
Mar | 2018-03-01 | e. HE15-18 | 15 | RRS | 2982 | 3195 | 213
Mar | 2018-03-01 | e. HE15-18 | 16 | RRS | 2982 | 3195 | 213
Mar | 2018-03-01 | e. HE15-18 | 17 | RRS | 2982 | 3195 | 213
Mar | 2018-03-01 | e. HE15-18 | 18 | RRS | 2982 | 3195 | 213
Mar | 2018-03-01 | f. HE19-22 | 19 | RRS | 2982 | 3195 | 213
Mar | 2018-03-01 | f. HE19-22 | 20 | RRS | 2982 | 3195 | 213
Mar | 2018-03-01 | f. HE19-22 | 21 | RRS | 2982 | 3195 | 213
Mar | 2018-03-01 | f. HE19-22 | 22 | RRS | 2982 | 3195 | 213
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3178 | 3335 | 157
Mar | 2018-03-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3178 | 3335 | 157
Apr | 2018-04-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3088 | 3195 | 107
Apr | 2018-04-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3088 | 3195 | 107
Apr | 2018-04-01 | b. HE3-6 | 3 | RRS | 3128 | 3239 | 111
Apr | 2018-04-01 | b. HE3-6 | 4 | RRS | 3128 | 3239 | 111
Apr | 2018-04-01 | b. HE3-6 | 5 | RRS | 3128 | 3239 | 111
Apr | 2018-04-01 | b. HE3-6 | 6 | RRS | 3128 | 3239 | 111
Apr | 2018-04-01 | c. HE7-10 | 7 | RRS | 3015 | 3156 | 141
Apr | 2018-04-01 | c. HE7-10 | 8 | RRS | 3015 | 3156 | 141
Apr | 2018-04-01 | c. HE7-10 | 9 | RRS | 3015 | 3156 | 141
Apr | 2018-04-01 | c. HE7-10 | 10 | RRS | 3015 | 3156 | 141
Apr | 2018-04-01 | d. HE11-14 | 11 | RRS | 2982 | 3041 | 59
Apr | 2018-04-01 | d. HE11-14 | 12 | RRS | 2982 | 3041 | 59
Apr | 2018-04-01 | d. HE11-14 | 13 | RRS | 2982 | 3041 | 59
Apr | 2018-04-01 | d. HE11-14 | 14 | RRS | 2982 | 3041 | 59
Apr | 2018-04-01 | e. HE15-18 | 15 | RRS | 2936 | 2991 | 55
Apr | 2018-04-01 | e. HE15-18 | 16 | RRS | 2936 | 2991 | 55
Apr | 2018-04-01 | e. HE15-18 | 17 | RRS | 2936 | 2991 | 55
Apr | 2018-04-01 | e. HE15-18 | 18 | RRS | 2936 | 2991 | 55
Apr | 2018-04-01 | f. HE19-22 | 19 | RRS | 2936 | 2991 | 55
Apr | 2018-04-01 | f. HE19-22 | 20 | RRS | 2936 | 2991 | 55
Apr | 2018-04-01 | f. HE19-22 | 21 | RRS | 2936 | 2991 | 55
Apr | 2018-04-01 | f. HE19-22 | 22 | RRS | 2936 | 2991 | 55
May | 2018-05-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3088 | 3195 | 107
May | 2018-05-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3088 | 3195 | 107
May | 2018-05-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2982 | 3041 | 59
May | 2018-05-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2982 | 3041 | 59
May | 2018-05-01 | b. HE3-6 | 3 | RRS | 3015 | 3041 | 26
May | 2018-05-01 | b. HE3-6 | 4 | RRS | 3015 | 3041 | 26
May | 2018-05-01 | b. HE3-6 | 5 | RRS | 3015 | 3041 | 26
May | 2018-05-01 | b. HE3-6 | 6 | RRS | 3015 | 3041 | 26
May | 2018-05-01 | c. HE7-10 | 7 | RRS | 2936 | 2949 | 13
May | 2018-05-01 | c. HE7-10 | 8 | RRS | 2936 | 2949 | 13
May | 2018-05-01 | c. HE7-10 | 9 | RRS | 2936 | 2949 | 13
May | 2018-05-01 | c. HE7-10 | 10 | RRS | 2936 | 2949 | 13
May | 2018-05-01 | d. HE11-14 | 11 | RRS | 2825 | 2774 | -51
May | 2018-05-01 | d. HE11-14 | 12 | RRS | 2825 | 2774 | -51
May | 2018-05-01 | d. HE11-14 | 13 | RRS | 2825 | 2774 | -51
May | 2018-05-01 | d. HE11-14 | 14 | RRS | 2825 | 2774 | -51
May | 2018-05-01 | e. HE15-18 | 15 | RRS | 2800 | 2800 | 0
May | 2018-05-01 | e. HE15-18 | 16 | RRS | 2800 | 2800 | 0
May | 2018-05-01 | e. HE15-18 | 17 | RRS | 2800 | 2800 | 0
May | 2018-05-01 | e. HE15-18 | 18 | RRS | 2800 | 2800 | 0
May | 2018-05-01 | f. HE19-22 | 19 | RRS | 2800 | 2800 | 0
May | 2018-05-01 | f. HE19-22 | 20 | RRS | 2800 | 2800 | 0
May | 2018-05-01 | f. HE19-22 | 21 | RRS | 2800 | 2800 | 0
May | 2018-05-01 | f. HE19-22 | 22 | RRS | 2800 | 2800 | 0
May | 2018-05-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2982 | 3041 | 59
May | 2018-05-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2982 | 3041 | 59
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2668 | 2651 | -17
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2668 | 2651 | -17
Jun | 2018-06-01 | b. HE3-6 | 3 | RRS | 2825 | 2774 | -51
Jun | 2018-06-01 | b. HE3-6 | 4 | RRS | 2825 | 2774 | -51
Jun | 2018-06-01 | b. HE3-6 | 5 | RRS | 2825 | 2774 | -51
Jun | 2018-06-01 | b. HE3-6 | 6 | RRS | 2825 | 2774 | -51
Jun | 2018-06-01 | c. HE7-10 | 7 | RRS | 2618 | 2651 | 33
Jun | 2018-06-01 | c. HE7-10 | 8 | RRS | 2618 | 2651 | 33
Jun | 2018-06-01 | c. HE7-10 | 9 | RRS | 2618 | 2651 | 33
Jun | 2018-06-01 | c. HE7-10 | 10 | RRS | 2618 | 2651 | 33
Jun | 2018-06-01 | d. HE11-14 | 11 | RRS | 2450 | 2381 | -69
Jun | 2018-06-01 | d. HE11-14 | 12 | RRS | 2450 | 2381 | -69
Jun | 2018-06-01 | d. HE11-14 | 13 | RRS | 2450 | 2381 | -69
Jun | 2018-06-01 | d. HE11-14 | 14 | RRS | 2450 | 2381 | -69
Jun | 2018-06-01 | e. HE15-18 | 15 | RRS | 2800 | 2800 | 0
Jun | 2018-06-01 | e. HE15-18 | 16 | RRS | 2800 | 2800 | 0
Jun | 2018-06-01 | e. HE15-18 | 17 | RRS | 2800 | 2800 | 0
Jun | 2018-06-01 | e. HE15-18 | 18 | RRS | 2800 | 2800 | 0
Jun | 2018-06-01 | f. HE19-22 | 19 | RRS | 2800 | 2800 | 0
Jun | 2018-06-01 | f. HE19-22 | 20 | RRS | 2800 | 2800 | 0
Jun | 2018-06-01 | f. HE19-22 | 21 | RRS | 2800 | 2800 | 0
Jun | 2018-06-01 | f. HE19-22 | 22 | RRS | 2800 | 2800 | 0
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2668 | 2651 | -17
Jun | 2018-06-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2668 | 2651 | -17
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2498 | 2517 | 19
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2498 | 2517 | 19
Jul | 2018-07-01 | b. HE3-6 | 3 | RRS | 2538 | 2562 | 24
Jul | 2018-07-01 | b. HE3-6 | 4 | RRS | 2538 | 2562 | 24
Jul | 2018-07-01 | b. HE3-6 | 5 | RRS | 2538 | 2562 | 24
Jul | 2018-07-01 | b. HE3-6 | 6 | RRS | 2538 | 2562 | 24
Jul | 2018-07-01 | c. HE7-10 | 7 | RRS | 2450 | 2517 | 67
Jul | 2018-07-01 | c. HE7-10 | 8 | RRS | 2450 | 2517 | 67
Jul | 2018-07-01 | c. HE7-10 | 9 | RRS | 2450 | 2517 | 67
Jul | 2018-07-01 | c. HE7-10 | 10 | RRS | 2450 | 2517 | 67
Jul | 2018-07-01 | d. HE11-14 | 11 | RRS | 2300 | 2300 | 0
Jul | 2018-07-01 | d. HE11-14 | 12 | RRS | 2300 | 2300 | 0
Jul | 2018-07-01 | d. HE11-14 | 13 | RRS | 2300 | 2300 | 0
Jul | 2018-07-01 | d. HE11-14 | 14 | RRS | 2300 | 2300 | 0
Jul | 2018-07-01 | e. HE15-18 | 15 | RRS | 2800 | 2800 | 0
Jul | 2018-07-01 | e. HE15-18 | 16 | RRS | 2800 | 2800 | 0
Jul | 2018-07-01 | e. HE15-18 | 17 | RRS | 2800 | 2800 | 0
Jul | 2018-07-01 | e. HE15-18 | 18 | RRS | 2800 | 2800 | 0
Jul | 2018-07-01 | f. HE19-22 | 19 | RRS | 2800 | 2800 | 0
Jul | 2018-07-01 | f. HE19-22 | 20 | RRS | 2800 | 2800 | 0
Jul | 2018-07-01 | f. HE19-22 | 21 | RRS | 2800 | 2800 | 0
Jul | 2018-07-01 | f. HE19-22 | 22 | RRS | 2800 | 2800 | 0
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2498 | 2517 | 19
Jul | 2018-07-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2498 | 2517 | 19
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2498 | 2517 | 19
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2498 | 2517 | 19
Aug | 2018-08-01 | b. HE3-6 | 3 | RRS | 2538 | 2600 | 62
Aug | 2018-08-01 | b. HE3-6 | 4 | RRS | 2538 | 2600 | 62
Aug | 2018-08-01 | b. HE3-6 | 5 | RRS | 2538 | 2600 | 62
Aug | 2018-08-01 | b. HE3-6 | 6 | RRS | 2538 | 2600 | 62
Aug | 2018-08-01 | c. HE7-10 | 7 | RRS | 2498 | 2517 | 19
Aug | 2018-08-01 | c. HE7-10 | 8 | RRS | 2498 | 2517 | 19
Aug | 2018-08-01 | c. HE7-10 | 9 | RRS | 2498 | 2517 | 19
Aug | 2018-08-01 | c. HE7-10 | 10 | RRS | 2498 | 2517 | 19
Aug | 2018-08-01 | d. HE11-14 | 11 | RRS | 2300 | 2300 | 0
Aug | 2018-08-01 | d. HE11-14 | 12 | RRS | 2300 | 2300 | 0
Aug | 2018-08-01 | d. HE11-14 | 13 | RRS | 2300 | 2300 | 0
Aug | 2018-08-01 | d. HE11-14 | 14 | RRS | 2300 | 2300 | 0
Aug | 2018-08-01 | e. HE15-18 | 15 | RRS | 2800 | 2800 | 0
Aug | 2018-08-01 | e. HE15-18 | 16 | RRS | 2800 | 2800 | 0
Aug | 2018-08-01 | e. HE15-18 | 17 | RRS | 2800 | 2800 | 0
Aug | 2018-08-01 | e. HE15-18 | 18 | RRS | 2800 | 2800 | 0
Aug | 2018-08-01 | f. HE19-22 | 19 | RRS | 2800 | 2800 | 0
Aug | 2018-08-01 | f. HE19-22 | 20 | RRS | 2800 | 2800 | 0
Aug | 2018-08-01 | f. HE19-22 | 21 | RRS | 2800 | 2800 | 0
Aug | 2018-08-01 | f. HE19-22 | 22 | RRS | 2800 | 2800 | 0
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2498 | 2517 | 19
Aug | 2018-08-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2498 | 2517 | 19
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2732 | 2705 | -27
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2732 | 2705 | -27
Sep | 2018-09-01 | b. HE3-6 | 3 | RRS | 2825 | 2774 | -51
Sep | 2018-09-01 | b. HE3-6 | 4 | RRS | 2825 | 2774 | -51
Sep | 2018-09-01 | b. HE3-6 | 5 | RRS | 2825 | 2774 | -51
Sep | 2018-09-01 | b. HE3-6 | 6 | RRS | 2825 | 2774 | -51
Sep | 2018-09-01 | c. HE7-10 | 7 | RRS | 2618 | 2651 | 33
Sep | 2018-09-01 | c. HE7-10 | 8 | RRS | 2618 | 2651 | 33
Sep | 2018-09-01 | c. HE7-10 | 9 | RRS | 2618 | 2651 | 33
Sep | 2018-09-01 | c. HE7-10 | 10 | RRS | 2618 | 2651 | 33
Sep | 2018-09-01 | d. HE11-14 | 11 | RRS | 2498 | 2427 | -71
Sep | 2018-09-01 | d. HE11-14 | 12 | RRS | 2498 | 2427 | -71
Sep | 2018-09-01 | d. HE11-14 | 13 | RRS | 2498 | 2427 | -71
Sep | 2018-09-01 | d. HE11-14 | 14 | RRS | 2498 | 2427 | -71
Sep | 2018-09-01 | e. HE15-18 | 15 | RRS | 2800 | 2800 | 0
Sep | 2018-09-01 | e. HE15-18 | 16 | RRS | 2800 | 2800 | 0
Sep | 2018-09-01 | e. HE15-18 | 17 | RRS | 2800 | 2800 | 0
Sep | 2018-09-01 | e. HE15-18 | 18 | RRS | 2800 | 2800 | 0
Sep | 2018-09-01 | f. HE19-22 | 19 | RRS | 2800 | 2800 | 0
Sep | 2018-09-01 | f. HE19-22 | 20 | RRS | 2800 | 2800 | 0
Sep | 2018-09-01 | f. HE19-22 | 21 | RRS | 2800 | 2800 | 0
Sep | 2018-09-01 | f. HE19-22 | 22 | RRS | 2800 | 2800 | 0
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2732 | 2705 | -27
Sep | 2018-09-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2732 | 2705 | -27
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 1 | RRS | 2982 | 3079 | 97
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 2 | RRS | 2982 | 3079 | 97
Oct | 2018-10-01 | b. HE3-6 | 3 | RRS | 3015 | 3156 | 141
Oct | 2018-10-01 | b. HE3-6 | 4 | RRS | 3015 | 3156 | 141
Oct | 2018-10-01 | b. HE3-6 | 5 | RRS | 3015 | 3156 | 141
Oct | 2018-10-01 | b. HE3-6 | 6 | RRS | 3015 | 3156 | 141
Oct | 2018-10-01 | c. HE7-10 | 7 | RRS | 2936 | 2991 | 55
Oct | 2018-10-01 | c. HE7-10 | 8 | RRS | 2936 | 2991 | 55
Oct | 2018-10-01 | c. HE7-10 | 9 | RRS | 2936 | 2991 | 55
Oct | 2018-10-01 | c. HE7-10 | 10 | RRS | 2936 | 2991 | 55
Oct | 2018-10-01 | d. HE11-14 | 11 | RRS | 2825 | 2871 | 46
Oct | 2018-10-01 | d. HE11-14 | 12 | RRS | 2825 | 2871 | 46
Oct | 2018-10-01 | d. HE11-14 | 13 | RRS | 2825 | 2871 | 46
Oct | 2018-10-01 | d. HE11-14 | 14 | RRS | 2825 | 2871 | 46
Oct | 2018-10-01 | e. HE15-18 | 15 | RRS | 2800 | 2800 | 0
Oct | 2018-10-01 | e. HE15-18 | 16 | RRS | 2800 | 2800 | 0
Oct | 2018-10-01 | e. HE15-18 | 17 | RRS | 2800 | 2800 | 0
Oct | 2018-10-01 | e. HE15-18 | 18 | RRS | 2800 | 2800 | 0
Oct | 2018-10-01 | f. HE19-22 | 19 | RRS | 2800 | 2800 | 0
Oct | 2018-10-01 | f. HE19-22 | 20 | RRS | 2800 | 2800 | 0
Oct | 2018-10-01 | f. HE19-22 | 21 | RRS | 2800 | 2800 | 0
Oct | 2018-10-01 | f. HE19-22 | 22 | RRS | 2800 | 2800 | 0
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 23 | RRS | 2982 | 3079 | 97
Oct | 2018-10-01 | a. HE1-2 & HE23-24 | 24 | RRS | 2982 | 3079 | 97
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3178 | 3239 | 61
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3178 | 3239 | 61
Nov | 2018-11-01 | b. HE3-6 | 3 | RRS | 3178 | 3239 | 61
Nov | 2018-11-01 | b. HE3-6 | 4 | RRS | 3178 | 3239 | 61
Nov | 2018-11-01 | b. HE3-6 | 5 | RRS | 3178 | 3239 | 61
Nov | 2018-11-01 | b. HE3-6 | 6 | RRS | 3178 | 3239 | 61
Nov | 2018-11-01 | c. HE7-10 | 7 | RRS | 3015 | 3079 | 64
Nov | 2018-11-01 | c. HE7-10 | 8 | RRS | 3015 | 3079 | 64
Nov | 2018-11-01 | c. HE7-10 | 9 | RRS | 3015 | 3079 | 64
Nov | 2018-11-01 | c. HE7-10 | 10 | RRS | 3015 | 3079 | 64
Nov | 2018-11-01 | d. HE11-14 | 11 | RRS | 2982 | 3041 | 59
Nov | 2018-11-01 | d. HE11-14 | 12 | RRS | 2982 | 3041 | 59
Nov | 2018-11-01 | d. HE11-14 | 13 | RRS | 2982 | 3041 | 59
Nov | 2018-11-01 | d. HE11-14 | 14 | RRS | 2982 | 3041 | 59
Nov | 2018-11-01 | e. HE15-18 | 15 | RRS | 2936 | 2991 | 55
Nov | 2018-11-01 | e. HE15-18 | 16 | RRS | 2936 | 2991 | 55
Nov | 2018-11-01 | e. HE15-18 | 17 | RRS | 2936 | 2991 | 55
Nov | 2018-11-01 | e. HE15-18 | 18 | RRS | 2936 | 2991 | 55
Nov | 2018-11-01 | f. HE19-22 | 19 | RRS | 2982 | 3041 | 59
Nov | 2018-11-01 | f. HE19-22 | 20 | RRS | 2982 | 3041 | 59
Nov | 2018-11-01 | f. HE19-22 | 21 | RRS | 2982 | 3041 | 59
Nov | 2018-11-01 | f. HE19-22 | 22 | RRS | 2982 | 3041 | 59
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3178 | 3239 | 61
Nov | 2018-11-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3178 | 3239 | 61
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 1 | RRS | 3128 | 3195 | 67
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 2 | RRS | 3128 | 3195 | 67
Dec | 2018-12-01 | b. HE3-6 | 3 | RRS | 3088 | 3195 | 107
Dec | 2018-12-01 | b. HE3-6 | 4 | RRS | 3088 | 3195 | 107
Dec | 2018-12-01 | b. HE3-6 | 5 | RRS | 3088 | 3195 | 107
Dec | 2018-12-01 | b. HE3-6 | 6 | RRS | 3088 | 3195 | 107
Dec | 2018-12-01 | c. HE7-10 | 7 | RRS | 3015 | 3079 | 64
Dec | 2018-12-01 | c. HE7-10 | 8 | RRS | 3015 | 3079 | 64
Dec | 2018-12-01 | c. HE7-10 | 9 | RRS | 3015 | 3079 | 64
Dec | 2018-12-01 | c. HE7-10 | 10 | RRS | 3015 | 3079 | 64
Dec | 2018-12-01 | d. HE11-14 | 11 | RRS | 2982 | 3041 | 59
Dec | 2018-12-01 | d. HE11-14 | 12 | RRS | 2982 | 3041 | 59
Dec | 2018-12-01 | d. HE11-14 | 13 | RRS | 2982 | 3041 | 59
Dec | 2018-12-01 | d. HE11-14 | 14 | RRS | 2982 | 3041 | 59
Dec | 2018-12-01 | e. HE15-18 | 15 | RRS | 2982 | 2991 | 9
Dec | 2018-12-01 | e. HE15-18 | 16 | RRS | 2982 | 2991 | 9
Dec | 2018-12-01 | e. HE15-18 | 17 | RRS | 2982 | 2991 | 9
Dec | 2018-12-01 | e. HE15-18 | 18 | RRS | 2982 | 2991 | 9
Dec | 2018-12-01 | f. HE19-22 | 19 | RRS | 2982 | 2991 | 9
Dec | 2018-12-01 | f. HE19-22 | 20 | RRS | 2982 | 2991 | 9
Dec | 2018-12-01 | f. HE19-22 | 21 | RRS | 2982 | 2991 | 9
Dec | 2018-12-01 | f. HE19-22 | 22 | RRS | 2982 | 2991 | 9
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 23 | RRS | 3128 | 3195 | 67
Dec | 2018-12-01 | a. HE1-2 & HE23-24 | 24 | RRS | 3128 | 3195 | 67