| NOGRR Number | 226 | NOGRR Title | Addition of Supplemental UFLS Stages |
| --- | --- | --- | --- |

| Date | November 30, 2022 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Nitika Mago |
| E-mail Address | nmago@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-6601 |
| Cell Number | (512) 689-1360 |
| Market Segment | Not Applicable |

Comments

ERCOT appreciates all the discussion on Nodal Operating Guide Revision Request (NOGRR) 226 and files these comments to address concerns related to the implementation timeline that were raised by Market Participants during the November 7, 2022 ROS Meeting.

ERCOT understands that Transmission Operators (TOs) may need as many as 18 months to implement the required relay changes across their footprint and hence an effective date of no earlier than October 1, 2024 is desired.  ERCOT also understands the need to provide clear guidance regarding Under-Frequency Load Shedding (UFLS) requirements while the anti-stall UFLS stages are being added in the field. Consequently, ERCOT is proposing edits that update paragraphs (1) and (5) of Section 2.6.1, Automatic Firm Load Shedding, such that:

- Following Public Utility Commission of Texas (PUCT) approval of NOGRR226, TOs may, but are not required, to have under-frequency relays set to provide Load relief in amounts up to the specifications in Table 2, Supplemental Anti-Stall UFLS Stages.

- Upon implementation of system changes associated with NOGRR226 but no earlier than October 1, 2024, the requirement to have under-frequency relays set to provide the required amounts of Load relief per the specifications in Table 2 will be mandatory.

ERCOT also proposes revisions to paragraph (3) to further clarify how TOs may use Load that would otherwise be used in standard UFLS stages 2 and 3 to provide the required Load relief in the anti-stall stages.  Lastly, for simplicity, ERCOT has also shortened the term “kicker/anti-stall UFLS stages” to “anti-stall UFLS stages”.

With the changes proposed in these comments, all of the revisions contemplated in NOGRR226 except the gray-box in paragraph (1) can become effective immediately upon PUCT approval, and TOs would be allowed to start adding anti-stall UFLS capability to their systems.  TOs would be required to install this additional capability by October 1, 2024.

Note that ERCOT is in the process of reviewing the settings in Table 1, Standard UFLS Stages, related to standard UFLS stages.  ERCOT is working on completing the required studies under PRC-006 as quickly as possible and intends to file a separate NOGRR on this topic, if appropriate.

Revised Cover Page Language

| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) adds provisions for Transmission Operator (TO) “anti-stall” automatic firm Load shedding at 59.5 Hz in order to improve reliability by mitigating the risk of a total system-wide Blackout. |
| --- | --- |

Revised Proposed Guide Language

2.6.1	Automatic Firm Load Shedding

(1)	At least 25% of the ERCOT System Load shall be equipped at all times with provisions for automatic Under-Frequency Load Shedding (UFLS) as described in this paragraph.  In the event of an under-frequency event, each Transmission Operator (TO) shall provide Load relief by shedding the required percentage of its Distribution Service Provider (DSP)-connected Load and transmission-level Customer Load using automatic under-frequency relays, as specified in Table 1, Standard UFLS Stages, below.  TOs may, but are not required to, provide supplemental anti-stall under-frequency Load relief in the amounts described in Table 2, Supplemental Anti-Stall UFLS Stages, below.  If the TOs provide supplemental anti-stall under-frequency Load relief, the under-frequency relays shall be set to use the frequency thresholds and time delays described in Table 2.  For the purposes of this paragraph, the TO Load will be the amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, when the ERCOT frequency drops to the 59.5 Hz threshold.  As such, TO Load that has already been removed from the system without restoration prior to the 59.5 Hz frequency threshold will not apply to meeting TO Load relief percentage requirements as stated in Table 1 and Table 2 below.

[NOGRR226: Replace paragraph (1) above with the following upon system implementation but no earlier than October 1, 2024:] (1) At least 25% of the ERCOT System Load shall be equipped at all times with provisions for automatic Under-Frequency Load Shedding (UFLS) as described in this paragraph. In the event of an under-frequency event, each Transmission Operator (TO) shall provide Load relief by shedding the required percentage of its Distribution Service Provider (DSP)-connected Load and transmission-level Customer Load using automatic under-frequency relays, as specified in the tables below. For the purposes of this paragraph, the TO Load will be the amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, when the ERCOT frequency drops to each identified frequency Hz threshold. As such, TO Load that has already been removed from the system without restoration prior to the 59.5 Hz frequency threshold will not apply to meeting TO Load relief percentage requirements as stated in Table 1 and Table 2 below.

Table 1: Standard UFLS Stages

| Frequency Threshold | TO Load Relief | Delay to Trip |
| --- | --- | --- |
| 59.3 Hz | At least 5% of the TO Load | No more than 30 cycles |
| 58.9 Hz | A total of at least 15% of the TO Load | No more than 30 cycles |
| 58.5 Hz | A total of at least 25% of the TO Load | No more than 30 cycles |

Table 2: Supplemental Anti-Stall UFLS Stages

| Frequency Threshold | TO Load Relief | Delay to Trip |
| --- | --- | --- |
| 59.5 Hz | At least 1.5% of the TO Load | 90 seconds |
| 59.5 Hz | A total of at least 3.0% of the TO Load | 120 seconds |
| 59.5 Hz | A total of at least 4.5% of the TO Load | 150 seconds |

(2)	ERCOT will, prior to the peak each year, survey each TO’s compliance with the automatic Load shedding requirements described in paragraph (1) above, and report its findings to the Technical Advisory Committee (TAC).  For purposes of determining a TO’s compliance with this annual survey requirement, TO Load will be the total amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, at the specified time of the survey.  The TO shall identify those circuits armed with under-frequency relays, the corresponding amount of Load, and identify the frequency threshold.  A TO shall not equip the entirety of its Load shed obligation in any one tier, and should endeavor to shed in controlled amounts that equal the difference between the TO Load relief required for each tier.  If ERCOT identifies potential reliability issues related to distribution of Load shed across the tiers, ERCOT may require the TO to redistribute Load relief closer to the minimum amount required after submitting ERCOT’s proposal to redistribute Load relief to the TO and considering any comments submitted by the TO regarding the proposal.  Compliance with this annual survey does not excuse the TO from compliance with the requirements of paragraph (1) above in an actual frequency event.  To assist TOs, ERCOT will provide the TO’s inventory, including substation and capacity amounts, of registered Load Resources in its area within ten Business Days of receiving a request in writing from a TO.

(3)	A TO may meet the Load relief requirements of the Supplemental anti-stall UFLS stages by utilizing Load that would otherwise be utilized to meet the 58.9 Hz and 58.5 Hz standard UFLS stages.  In this circumstance, the TO’s Load relief responsibility at the 58.9 and 58.5 Hz standard UFLS stages is reduced by the amount of Load already shed in the supplemental anti-stall UFLS stages.  A TO may not meet the Load relief requirements of the supplemental anti-stall UFLS stages by utilizing Load that the TO needs to meet the 59.3 Hz standard UFLS stage.

(4)	Additional under-frequency relays may be installed on Transmission Facilities with the approval of ERCOT provided the relays are set at 58.0 Hz or below, are not directional, and have at least 2.0 seconds time delay.  A DSP may by mutual agreement arrange to have all or part of its automatic Load shedding requirement performed by another entity.  ERCOT will be notified and provided with the details of any such arrangement prior to implementation.

(5)	DSPs shall ensure, to the extent possible, and under the direction of ERCOT, that Loads equipped with under-frequency relays are dispersed geographically throughout the ERCOT Region to minimize the impact of Load shedding within a given geographical area.  Customers equipped with under-frequency relays shall be dispersed without regard to which Load Serving Entity (LSE) serves the customer.  DSPs shall ensure that Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs) are connected to circuits that are not subject to disconnection during UFLS events, except as permitted by Protocol Section 3.8.6, Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs).  DSPs shall ensure that the under-frequency relays connected to each Load will operate with a fixed time delay as specified in paragraph (1) above.  Total time from the time when a sustained under-frequency condition first reaches one of the values specified above to the time Load is interrupted should be no more than the fixed time delay specified in paragraph (1) above plus 10 cycles, including all relay and breaker operating times.  If the frequency drops below 58.5 Hz, ERCOT shall determine additional steps to continue operation.

(6)	If a loss of Load occurs due to the operation of under-frequency relays, a DSP or its designee may rotate the physical Load interrupted to minimize the duration of interruption experienced by individual Customers or to restore the availability of under-frequency Load-shedding capability.  In no event shall the initial total amount of Load without service be decreased without the approval of ERCOT.  TOs, in coordination with DSPs, shall make every reasonable attempt to restore Load, either by automatic or manual means, to preserve system integrity.  Restoration of any Load shed by UFLS systems, including supplemental anti-stall UFLS Load, shall be coordinated with ERCOT by the TO.  In the event frequency drops below any of the frequency thresholds specified in the tables in paragraph (1) above, and a TO’s UFLS relays that previously activated as a result of reaching that same frequency threshold have not been restored since the previous excursion, the Load on the feeders controlled by those relays shall be counted toward the TO’s satisfaction of the percentages in paragraph (1) above for that subsequent frequency excursion.