## Introduction
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## 2023_Transmission_Losses
TRANSMISSION LOSS FACTORS for 2023 as of 11/04/22
Data from Seasonal SSWG Base Cases Updated with updates received by 11/04/22
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN (9) NOIE INTERNAL TOTAL |  |  |  |  | CPS (5) NOIE INTERNAL TOTAL |  |  |  |  | COG (20) NOIE INTERNAL TOTAL |  |  |  |  | GEUS (21) NOIE INTERNAL TOTAL |  |  |  |  | COD (19) NOIE INTERNAL TOTAL |  |  |  |  | BPUB (15) NOIE INTERNAL TOTAL |  |  |  |  | BTU (22) NOIE INTERNAL TOTAL |  |  |  |  | COCS (23) NOIE INTERNAL TOTAL |  |  |  |  | LPL (31) NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 2023_SPG1 | 85621.2 | 83957.2 | 1499.22 | 1655.34 | 615.5 | 2546.9 | 34.17 | 34.5 | 1965.9 | 3914 | 4529 | 31.98 | 37.3 | 652.3 | 323.7 | 341.5 | 2.8 | 3.5 | 21.3 | 24.6 | 71.3 | 0.09 | 0.1 | 46.8 | 47 | 659 | 0.34 | 0.5 | 612.5 | 101 | 307.9 | 0.72 | 0.9 | 207.8 | 108.5 | 373.2 | 3.98 | 4.4 | 269.1 | 0 | 179.1 | 0.42 | 0.4 | 179.5 | 76 | 243.2 | 0.7 | 0.9 | 168.1
Spring Off Peak | 2023_SPG2 | 60259.6 | 58929.3 | 1217.88 | 1323.98 | 474 | 1468 | 12.13 | 12.1 | 1006.1 | 2507.7 | 2491 | 17.37 | 20.1 | 3.4 | 418.2 | 171 | 1.86 | 3.1 | -244.1 | 0 | 50 | 0.04 | 0 | 50 | 0 | 573.7 | 0.22 | 0.2 | 573.9 | 101 | 152.7 | 0.2 | 0.4 | 52.1 | 108.5 | 187.6 | 1.27 | 1.7 | 80.8 | 0 | 53.8 | 0.04 | 0 | 53.8 | 76 | 180.8 | 0.8 | 1 | 105.8
Summer On Peak | 2023_SUM1 | 106077.6 | 103900.5 | 1936.7 | 2139.38 | 1383.7 | 2871 | 59.44 | 61 | 1548.3 | 4786.3 | 5532 | 45.57 | 53 | 798.7 | 451 | 493.4 | 6.47 | 7.7 | 50.1 | 99.6 | 116 | 0.42 | 0.8 | 17.2 | 225 | 673.9 | 0.99 | 1.7 | 450.6 | 103 | 329.2 | 0.87 | 1.1 | 227.3 | 260 | 473.5 | 6.08 | 7 | 220.5 | 0 | 228.9 | 0.53 | 0.5 | 229.4 | 107 | 454.9 | 1.71 | 2 | 349.9
Summer Off Peak | 2023_SUM2 | 70489.6 | 69024.5 | 1336.96 | 1459.49 | 1000 | 1592 | 21.53 | 22.7 | 614.7 | 4062.7 | 3153 | 25.66 | 31.5 | -878.2 | 149.7 | 246 | 1.62 | 1.9 | 98.2 | 0 | 69.3 | 0.07 | 0.1 | 69.4 | 0 | 503.5 | 0.09 | 0.1 | 503.6 | 98 | 167.3 | 0.24 | 0.4 | 69.7 | 150 | 245.3 | 1.75 | 2.2 | 97.5 | 0 | 62.9 | 0.06 | 0.1 | 63 | 76 | 224.1 | 0.94 | 1.1 | 149.2
Fall On Peak | 2023_FAL1 | 89545.3 | 87777.5 | 1601.71 | 1763.08 | 1166.9 | 2545 | 37.37 | 38.9 | 1417 | 3396.1 | 4610 | 27.92 | 33.1 | 1247 | 176.3 | 292.2 | 2.74 | 3 | 118.9 | 24.6 | 104.2 | 0.19 | 0.2 | 79.8 | 82.8 | 622.2 | 0.41 | 0.5 | 539.9 | 99 | 300.2 | 0.74 | 0.9 | 202.1 | 11 | 446.9 | 6.45 | 6.5 | 442.4 | 0 | 183.1 | 0.64 | 0.6 | 183.7 | 76 | 352.3 | 1.25 | 1.4 | 277.7
Fall Off Peak | 2023_FAL2 | 61518.7 | 60208.5 | 1200.97 | 1308.5 | 473 | 1461 | 19.1 | 19.1 | 1007.1 | 3754.2 | 2582 | 23.26 | 27.8 | -1144.4 | 408.6 | 147 | 1.91 | 2.9 | -258.7 | 0 | 60.6 | 0.05 | 0.1 | 60.7 | 0 | 467.5 | 0.19 | 0.2 | 467.7 | 99 | 143.5 | 0.19 | 0.4 | 44.9 | 119.5 | 227.1 | 1.92 | 2.4 | 110 | 0 | 56 | 0.08 | 0.1 | 56.1 | 76 | 173.3 | 1.35 | 1.5 | 98.8
Winter On Peak | 2024_WIN1 | 99438.1 | 97337.1 | 1907.42 | 2093.19 | 1429.4 | 2512 | 50.27 | 51.7 | 1134.3 | 4846.2 | 4828 | 44.32 | 51.7 | 33.5 | 466 | 379.3 | 5.24 | 6.6 | -80.1 | 99.6 | 80.9 | 0.36 | 0.8 | -17.9 | 226 | 573.7 | 0.73 | 1.4 | 349.1 | 116 | 290.2 | 0.73 | 0.9 | 175.1 | 271 | 432.1 | 5.9 | 6.9 | 168 | 0 | 183 | 0.35 | 0.3 | 183.3 | 107 | 379.9 | 1.46 | 1.7 | 274.6
Winter Off Peak | 2024_WIN2 | 75531.4 | 73920.3 | 1464.57 | 1605.59 | 1036 | 1424 | 15.14 | 16.4 | 404.4 | 3828 | 3186 | 22.06 | 27.1 | -614.9 | 113.2 | 188 | 1.93 | 2.3 | 77.1 | 0 | 57.5 | 0.05 | 0 | 57.5 | 0 | 503.5 | 0.32 | 0.3 | 503.8 | 110 | 176.9 | 0.32 | 0.5 | 67.4 | 153 | 296.2 | 2.37 | 2.8 | 146 | 0 | 132.3 | 0.15 | 0.1 | 132.4 | 76 | 217 | 1.55 | 1.7 | 142.7
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | LPL Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 2023_SPG1 | 2721.52 | 1463.98 | 723.35 | 32.49 | 114.9 | 0 | 0 | 5056.24 |  | 9251.1 | 4123.3 | 5127.8 | 75.2 | 2023_SPG1
Spring Off Peak | 2023_SPG2 | 2721.52 | 1463.98 | 672.71 | 16.33 | 114.9 | 0 | 0 | 4989.44 |  | 5328.6 | 1681.8 | 3646.8 | 33.93 | 2023_SPG2
Summer On Peak | 2023_SUM1 | 2721.52 | 1483.26 | 723.35 | 40.32 | 114.9 | 0 | 0 | 5083.35 |  | 11172.8 | 3892 | 7280.8 | 122.08 | 2023_SUM1
Summer Off Peak | 2023_SUM2 | 2721.52 | 1452.98 | 629.57 | 20.88 | 114.9 | 0 | 0 | 4939.85 |  | 6263.4 | 787.1 | 5476.3 | 51.96 | 2023_SUM2
Fall On Peak | 2023_FAL1 | 2721.52 | 1459.98 | 723.35 | 38.06 | 114.9 | 0 | 0 | 5057.81 |  | 9456.1 | 4508.5 | 4947.6 | 77.71 | 2023_FAL1
Fall Off Peak | 2023_FAL2 | 2721.52 | 1459.98 | 635.3 | 19.33 | 114.9 | 0 | 0 | 4951.03 |  | 5318 | 442.2 | 4875.8 | 48.05 | 2023_FAL2
Winter On Peak | 2024_WIN1 | 2721.52 | 1496.89 | 723.35 | 36.41 | 138.7 | 0 | 0 | 5116.87 |  | 9659.1 | 2219.9 | 7439.2 | 109.36 | 2024_WIN1
Winter Off Peak | 2024_WIN2 | 2721.52 | 1496.89 | 641.03 | 24.96 | 138.7 | 0 | 0 | 5023.1 |  | 6181.4 | 916.4 | 5265 | 43.89 | 2024_WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL |  |  |  |  | LPL NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 80564.96 | 55270.16 | 1.861% | 2.204% |  | 2546.9 | 1468 | 1.324% | 0.8195% |  | 4529 | 2491 | 0.7012% | 0.6925% |  | 341.5 | 171 | 0.8132% | 1.076% |  | 71.3 | 50 | 0.1261% | 0.07994% |  | 659 | 573.7 | 0.05157% | 0.03833% |  | 307.9 | 152.7 | 0.2333% | 0.1308% |  | 373.2 | 187.6 | 1.055% | 0.6724% |  | 179.1 | 53.8 | 0.234% | 0.07429% |  | 243.2 | 180.8 | 0.287% | 0.4405%
SUMMER | 100994.25 | 65549.75 | 1.918% | 2.04% |  | 2871 | 1592 | 2.028% | 1.334% |  | 5532 | 3153 | 0.817% | 0.8073% |  | 493.4 | 246 | 1.294% | 0.6542% |  | 116 | 69.3 | 0.3608% | 0.1009% |  | 673.9 | 503.5 | 0.1467% | 0.01787% |  | 329.2 | 167.3 | 0.2636% | 0.1432% |  | 473.5 | 245.3 | 1.268% | 0.7084% |  | 228.9 | 62.9 | 0.231% | 0.0953% |  | 454.9 | 224.1 | 0.3745% | 0.4177%
FALL | 84487.49 | 56567.67 | 1.896% | 2.123% |  | 2545 | 1461 | 1.447% | 1.29% |  | 4610 | 2582 | 0.602% | 0.8928% |  | 292.2 | 147 | 0.929% | 1.283% |  | 104.2 | 60.6 | 0.182% | 0.08244% |  | 622.2 | 467.5 | 0.06585% | 0.04063% |  | 300.2 | 143.5 | 0.2459% | 0.1322% |  | 446.9 | 227.1 | 1.423% | 0.8384% |  | 183.1 | 56 | 0.3483% | 0.1427% |  | 352.3 | 173.3 | 0.3536% | 0.773%
WINTER | 94321.23 | 70508.3 | 2.022% | 2.077% |  | 2512 | 1424 | 1.962% | 1.052% |  | 4828 | 3186 | 0.9096% | 0.6876% |  | 379.3 | 188 | 1.363% | 1.016% |  | 80.9 | 57.5 | 0.443% | 0.08688% |  | 573.7 | 503.5 | 0.1271% | 0.06351% |  | 290.2 | 176.9 | 0.2509% | 0.1806% |  | 432.1 | 296.2 | 1.347% | 0.7938% |  | 183 | 132.3 | 0.1909% | 0.1133% |  | 379.9 | 217 | 0.3828% | 0.7092%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL |  |  |  |  | LPL NOIE INTERNAL
| SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC
SPRING | -1.3545e-05 | 2.9521 |  |  |  | 0.00046746 | 0.13329 |  |  |  | 4.2608e-06 | 0.68187 |  |  |  | -0.0015412 | 1.3396 |  |  |  | 0.0021658 | -0.028355 |  |  |  | 0.00015514 | -0.050674 |  |  |  | 0.00066039 | 0.029963 |  |  |  | 0.0020624 | 0.28552 |  |  |  | 0.0012742 | 0.0057398 |  |  |  | -0.0024603 | 0.88536
SUMMER | -3.4414e-06 | 2.2652 |  |  |  | 0.00054263 | 0.47048 |  |  |  | 4.1043e-06 | 0.79432 |  |  |  | 0.0025873 | 0.017742 |  |  |  | 0.0055643 | -0.2847 |  |  |  | 0.00075598 | -0.36276 |  |  |  | 0.00074324 | 0.018905 |  |  |  | 0.0024514 | 0.10702 |  |  |  | 0.00081752 | 0.043876 |  |  |  | -0.00018719 | 0.45965
FALL | -8.1402e-06 | 2.5835 |  |  |  | 0.00014453 | 1.0793 |  |  |  | -0.0001434 | 1.2631 |  |  |  | -0.0024356 | 1.6407 |  |  |  | 0.0022837 | -0.055952 |  |  |  | 0.00016307 | -0.035609 |  |  |  | 0.00072538 | 0.028137 |  |  |  | 0.0026587 | 0.23456 |  |  |  | 0.0016181 | 0.052038 |  |  |  | -0.0023431 | 1.179
WINTER | -2.3055e-06 | 2.2397 |  |  |  | 0.00083632 | -0.1389 |  |  |  | 0.00013519 | 0.25692 |  |  |  | 0.0018113 | 0.67564 |  |  |  | 0.01522 | -0.78825 |  |  |  | 0.00090552 | -0.39242 |  |  |  | 0.00062094 | 0.070722 |  |  |  | 0.004071 | -0.41205 |  |  |  | 0.0015314 | -0.089353 |  |  |  | -0.0020036 | 1.144
EFFECTIVE DATES | SEASON
03/01/2023 - 05/31/2023 | SPRING
06/01/2023 - 09/30/2023 | SUMMER
10/01/2023 - 11/30/2023 | FALL
12/01/2023 - 02/29/2024 | WINTER