| NOGRR Number | 226 | NOGRR Title | Addition of Supplemental UFLS Stages |
| --- | --- | --- | --- |
| Date of Decision |  | December 20, 2022 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | January 27, 2023 |  |
| Priority and Rank Assigned |  | Priority – 2023; Rank – 3900 |  |
| Nodal Operating Guide Sections Requiring Revision |  | - 2.6.1, Automatic Firm Load Shedding |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) adds provisions for Transmission Operator (TO) “anti-stall” automatic firm Load shedding at 59.5 Hz in order to improve reliability by mitigating the risk of a total system-wide Blackout. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or /directed by the ERCOT Board)./ Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | On February 15, 2021 the system-wide frequency fell below 59.4 Hz for approximately four minutes and twenty-four seconds but did not fall below 59.3 Hz which would have triggered TO Load shedding and increased the system frequency above 59.4 Hz. Generators are required to operate their generation reliably and without tripping for frequencies above 59.4 Hz. When the frequency falls below 59.4 Hz, there is risk of damage to turbine blades. In order to avoid this damage, a relay is triggered that will trip the generator Off-Line after nine minutes. To mitigate this issue, this NOGRR proposes that TOs make automatic Load reductions in small steps when frequency degrades to 59.5 Hz, with the goal of avoiding further frequency declines. LCRA recommends that the Dynamics Working Group (DWG) review the 58.9 Hz and 58.5 Hz TO Load shedding relay set points and determine if any changes are needed to these set points. |  |
| ROS Decision |  | On 6/3/21, ROS voted unanimously to table NOGRR226 and refer the issue to the DWG, the Operations Working Group (OWG), and the Performance, Disturbance, Compliance Working Group (PDCWG). All Market Segments participated in the vote. On 9/1/22, ROS voted unanimously to recommend approval of NOGRR226 as amended by the 8/31/22 CenterPoint Energy comments as revised by ROS. All Market Segments participated in the vote. On 9/29/22, ROS voted unanimously to table NOGRR226. All Market Segments participated in the vote. On 11/7/22, ROS voted unanimously to endorse and forward to TAC the 9/1/22 ROS Report and 11/1/22 Impact Analysis for NOGRR226, with a recommended priority of 2023 and rank of 3900. All Market Segments participated in the vote. |  |
| Summary of ROS Discussion |  | On 6/3/21, participants discussed the recent history of system-wide frequency drops and the need for further review of NOGRR226 to explore the possibility of unintended consequences. On 9/1/22, participants reviewed the 8/17/22 Joint TOs comments and the 8/31/22 CenterPoint Energy comments, and offered additional clarifications, including a title change, and discussed that NOGRR226 should be implemented 18 months after approval. On 9/29/22, participants reviewed the 9/22/22 ERCOT comments and expressed a need to table NOGRR226 awaiting the Impact Analysis. On 11/7/22, participants reviewed the 11/1/22 Impact Analysis, discussed NOGRR226’s implementation requirements and effective date; and how best to capture compliance language. ERCOT committed to filing additional comments providing effective date language. |  |
| TAC Decision |  | On 12/5/22, TAC voted to recommend approval of NOGRR226 as recommended by ROS in the 11/7/22 ROS Report as amended by the 11/30/22 ERCOT comments as revised by TAC; with a proposed effective date of January 20, 2023. There was one abstention from the Independent Retail Electric Provider (IREP) (Reliant) Market Segment. All Market Segments participated in the vote. |  |
| Summary of TAC Discussion |  | On 12/5/22, participants reviewed the ERCOT Opinion, ERCOT Market Impact Statement, Independent Market Monitor (IMM) Opinion, and 11/30/22 ERCOT comments. ERCOT Staff proposed edits to incorporate references to the September 29, 2022 ROS decision and discussion. |  |
| Board Decision |  | On 12/20/22, the ERCOT Board voted unanimously to recommend approval of NOGRR226 as recommended by TAC in the 12/5/22 TAC Report with a proposed effective date of January 27, 2023. |  |

| Opinions |  |
| --- | --- |
| Credit Work Group Review | Not Applicable |
| Independent Market Monitor Opinion | IMM has no opinion on NOGRR226. |
| ERCOT Opinion | ERCOT supports approval of NOGRR226. |
| ERCOT Market Impact Statement | ERCOT Staff has reviewed NOGRR226 and believes that the addition of supplemental anti-stall Under-Frequency Load Shed (UFLS) stages that are set to operate whenever frequency drops below 59.5 Hz with a certain time delay provides a positive market impact that will, in the event of a slow frequency decline, address the mismatch issue between generator under-frequency protection that occurs at 59.4 Hz and standard UFLS that triggers at 59.3 Hz. |

| Sponsor |  |
| --- | --- |
| Name | John Dumas |
| E-mail Address | John.Dumas@lcra.org |
| Company | Lower Colorado River Authority |
| Phone Number | 512-913-9399 |
| Cell Number |  |
| Market Segment | Cooperative |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Jordan Troublefield |
| E-Mail Address | Jordan.Troublefield@ercot.com |
| Phone Number | 512-248-6521 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| LCRA 080221 | Requested ROS continue to table NOGRR226 |
| Oncor 081622 | Expressed concern that NOGRR226 as proposed could have further exacerbated generator stability concerns for units that were already in a fragile state under the system conditions experienced in February 2021 and proposed revisions |
| Joint TOs 081722 | Adjusted three parameters in the proposed Table 2, Supplemental Kicker/Anti-Stall UFLS Stages, in paragraph (1) of Section 2.6.1 |
| CenterPoint Energy 083122 | Modified language in paragraphs (1) and (5) of Section 2.6.1 |
| ERCOT 092222 | Proposed completion of the Impact Analysis for NOGRR226 prior to the November 7, 2022 ROS meeting |
| PRS 111622 | Endorsed the ROS-recommended priority of 2023 and rank of 3900 |
| ERCOT 113022 | Proposed edits regarding a staggered implementation plan, allowing for the entirety of NOGRR226 to be made effective immediately following PUCT approval (January 20, 2023), with the exception of the greybox in paragraph (1) which will be effective upon system implementation but no earlier than October 1, 2024 |

Market Rules Notes

Please note the baseline language in the following section has been updated to reflect the incorporation of the following NOGRR(s) into the Nodal Operating Guide:

- NOGRR212, Related to NPRR1016, Clarify Requirements for Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs) (unboxed 1/1/22)

  - Section 2.6.1

- NOGRR233, Related to NPRR1094, Allow Under Frequency Relay Load to be Manually Shed During EEA3 (incorporated 12/17/21)

  - Section 2.6.1

Proposed Guide Language Revision

2.6.1	Automatic Firm Load Shedding

(1)	At least 25% of the ERCOT System Load shall be equipped at all times with provisions for automatic Under-Frequency Load Shedding (UFLS) as described in this paragraph.  In the event of an under-frequency event, each Transmission Operator (TO) shall provide Load relief by shedding the required percentage of its Distribution Service Provider (DSP)-connected Load and transmission-level Customer Load using automatic under-frequency relays, as specified in Table 1, Standard UFLS Stages, below.  TOs may, but are not required to, provide supplemental anti-stall under-frequency Load relief in the amounts described in Table 2, Supplemental Anti-Stall UFLS Stages, below.  If the TOs provide supplemental anti-stall under-frequency Load relief, the under-frequency relays shall be set to use the frequency thresholds and time delays described in Table 2.  For the purposes of this paragraph, the TO Load will be the amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, when the ERCOT frequency drops to the 59.5 Hz threshold.  As such, TO Load that has already been removed from the system without restoration prior to the 59.5 Hz frequency threshold will not apply to meeting TO Load relief percentage requirements as stated in Table 1 and Table 2 below.

[NOGRR226: Replace paragraph (1) above with the following upon system implementation but no earlier than October 1, 2024:] (1) At least 25% of the ERCOT System Load shall be equipped at all times with provisions for automatic Under-Frequency Load Shedding (UFLS) as described in this paragraph. In the event of an under-frequency event, each Transmission Operator (TO) shall provide Load relief by shedding the required percentage of its Distribution Service Provider (DSP)-connected Load and transmission-level Customer Load using automatic under-frequency relays, as specified in the tables below. For the purposes of this paragraph, the TO Load will be the amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, when the ERCOT frequency drops to each identified frequency Hz threshold. As such, TO Load that has already been removed from the system without restoration prior to the 59.5 Hz frequency threshold will not apply to meeting TO Load relief percentage requirements as stated in Table 1 and Table 2 below.

Table 1: Standard UFLS Stages

| Frequency Threshold | TO Load Relief | Delay to Trip |
| --- | --- | --- |
| 59.3 Hz | At least 5% of the TO Load | No more than 30 cycles |
| 58.9 Hz | A total of at least 15% of the TO Load | No more than 30 cycles |
| 58.5 Hz | A total of at least 25% of the TO Load | No more than 30 cycles |

Table 2: Supplemental Anti-Stall UFLS Stages

| Frequency Threshold | TO Load Relief | Delay to Trip |
| --- | --- | --- |
| 59.5 Hz | At least 1.5% of the TO Load | 90 seconds |
| 59.5 Hz | A total of at least 3.0% of the TO Load | 120 seconds |
| 59.5 Hz | A total of at least 4.5% of the TO Load | 150 seconds |

(2)	ERCOT will, prior to the peak each year, survey each TO’s compliance with the automatic Load shedding requirements described in paragraph (1) above, and report its findings to the Technical Advisory Committee (TAC).  For purposes of determining a TO’s compliance with this annual survey requirement, TO Load will be the total amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, at the specified time of the survey.  The TO shall identify those circuits armed with under-frequency relays, the corresponding amount of Load, and identify the frequency threshold.  A TO shall not equip the entirety of its Load shed obligation in any one tier, and should endeavor to shed in controlled amounts that equal the difference between the TO Load relief required for each tier.  If ERCOT identifies potential reliability issues related to distribution of Load shed across the tiers, ERCOT may require the TO to redistribute Load relief closer to the minimum amount required after submitting ERCOT’s proposal to redistribute Load relief to the TO and considering any comments submitted by the TO regarding the proposal.  Compliance with this annual survey does not excuse the TO from compliance with the requirements of paragraph (1) above in an actual frequency event.  To assist TOs, ERCOT will provide the TO’s inventory, including substation and capacity amounts, of registered Load Resources in its area within ten Business Days of receiving a request in writing from a TO.

(3)	A TO may meet the Load relief requirements of the Supplemental anti-stall UFLS stages by utilizing Load that would otherwise be utilized to meet the 58.9 Hz and 58.5 Hz standard UFLS stages.  In this circumstance, the TO’s Load relief responsibility at the 58.9 and 58.5 Hz standard UFLS stages is reduced by the amount of Load already shed in the supplemental anti-stall UFLS stages.  A TO may not meet the Load relief requirements of the supplemental anti-stall UFLS stages by utilizing Load that the TO needs to meet the 59.3 Hz standard UFLS stage.

(4)	Additional under-frequency relays may be installed on Transmission Facilities with the approval of ERCOT provided the relays are set at 58.0 Hz or below, are not directional, and have at least 2.0 seconds time delay.  A DSP may by mutual agreement arrange to have all or part of its automatic Load shedding requirement performed by another entity.  ERCOT will be notified and provided with the details of any such arrangement prior to implementation.

(5)	DSPs shall ensure, to the extent possible, and under the direction of ERCOT, that Loads equipped with under-frequency relays are dispersed geographically throughout the ERCOT Region to minimize the impact of Load shedding within a given geographical area.  Customers equipped with under-frequency relays shall be dispersed without regard to which Load Serving Entity (LSE) serves the customer.  DSPs shall ensure that Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs) are connected to circuits that are not subject to disconnection during UFLS events, except as permitted by Protocol Section 3.8.6, Distribution Generation Resources (DGRs) and Distribution Energy Storage Resources (DESRs).  DSPs shall ensure that the under-frequency relays connected to each Load will operate with a fixed time delay as specified in paragraph (1) above.  Total time from the time when a sustained under-frequency condition first reaches one of the values specified above to the time Load is interrupted should be no more than the fixed time delay specified in paragraph (1) above plus 10 cycles, including all relay and breaker operating times.  If the frequency drops below 58.5 Hz, ERCOT shall determine additional steps to continue operation.

(6)	If a loss of Load occurs due to the operation of under-frequency relays, a DSP or its designee may rotate the physical Load interrupted to minimize the duration of interruption experienced by individual Customers or to restore the availability of under-frequency Load-shedding capability.  In no event shall the initial total amount of Load without service be decreased without the approval of ERCOT.  TOs, in coordination with DSPs, shall make every reasonable attempt to restore Load, either by automatic or manual means, to preserve system integrity.  Restoration of any Load shed by UFLS systems, including supplemental anti-stall UFLS Load, shall be coordinated with ERCOT by the TO.  In the event frequency drops below any of the frequency thresholds specified in the tables in paragraph (1) above, and a TO’s UFLS relays that previously activated as a result of reaching that same frequency threshold have not been restored since the previous excursion, the Load on the feeders controlled by those relays shall be counted toward the TO’s satisfaction of the percentages in paragraph (1) above for that subsequent frequency excursion.