## Index
RTP Scope Section Number | Input Assumption | Status | Date
Transmission Topology
3.1.1 | Start Cases | Final | 2022-01-04
3.1.2 | RPG Projects Backed Out For Lack of Approval or Moved Due to ISD Change | Final | 2022-02-01
3.1.2 | Recently Approved RPG Projects | Final | 2022-11-22
3.1.2 | Model Updates & Corrections | Final | 2022-10-06
3.1.3 | Transmission & Generation Outages | Final | 2022-09-14
3.1.5 | Temperatures Used in Dynamic Rating Calculation | Final | 2022-01-04
Generation
3.2.1 | Generation Additions, Retirements and Mothballs | Final | 2022-04-28
3.2.2 | Renewable Generation Dispatch | Final | 2022-04-15
3.2.3 | Switchable Generation | Final | 2022-04-28
3.2.4 | DC Tie Modeling and Dispatch | Final | 2022-04-15
3.2.5 | Reserve Requirement | Final | 2022-01-04
3.2.6 | Fuel Price Assumptions | Final | 2022-04-12
Demand
3.3 | Load Forecast (Reliability) 90/10 Forecast SSWG Forecast Bounded Higher of Calculations RTP Summer Peak Case Forecast RTP Min Load Case Forecast | Final | 2022-11-05
Other Studies
4.2.2 | Sensitivity Analysis | Final | 2022-11-30

## Start Cases
Date Last Updated: | 2022-01-04 | Back
Status | Final
SSWG Case Version: | 21SSWG Update 1 Final - October 22, 2021
On Peak Cases:
21SSWG_2024_SUM1_U1_FINAL_10222021.raw
21SSWG_2025_SUM1_U1_FINAL_10222021.raw
21SSWG_2027_SUM1_U1_FINAL_10222021.raw
21SSWG_2028_SUM1_U1_FINAL_10222021.raw
Off Peak Case:
21SSWG_2025_MIN_U1_FINAL_10222021.raw

## RPG Projects Moved or Removed
Date Last Updated: | 2022-02-01 |  | Back
Status | Final
Based on TPIT dated:
RPG Projects Removed from the RTP Cases
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number
64239 | Vineyard Switch-North Lake Switch 138 kV Line |  | North Lake Switch | Vineyard Switch |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 |  | 2023-05-15 | 138 | Tier 3 |  |  |  | 2022, 2386, 12013, 15030, 15035 | Y | 64240 | 64239
64382 | Bowman Auto 1 Upgrade | Upgrade existing Bowman Auto #1 300 MVA to 600 MVA. | Bowman | Bowman |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6897 |  | 2023-05-15 | 345 | Tier 3 | N/A | N/A | N/A | 1422, 1423, 29048 | Y | 64383 | 64382
5467 | Nacogdoches Southeast_Redland 345kV Line | Establish a new 345kV Line between Nacogdoches Southeast Switch and Redland Switch | Nacogdoches Southeast | Redland |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6898 |  | 2023-12-14 | 345 | Tier 2 | 2020-10-01 |  |  | 3119, 3321 | Y | 13171 | 5467
5466 | Redland Switch 345/138 kV Autotransformer | Install new 345/138 kV Autotransformer at Redland Switch previously known as Herty North | Redland | Redland |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6899 |  | 2023-12-15 | 345 | Tier 3 | 2020-10-01 |  |  | 3319, 3321, 3322 | Y | 13170 | 5466
5475 | Lufkin Switch - Redland Switch 345 kV Line | Construct a new 345 kV Line from Lufkin Switch to Redland Switch | Lufkin Switch | Redland Switch |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6900 |  | 2023-12-15 | 345 | Tier 2 | 2020-10-01 |  |  | 3117, 3321 | Y | 13180 | 5475
62693 | Courtney Creek - Yucca Drive 69 kV Line Conversion to 138 kV | Add Courtney Creek - Yucca Drive 69 kV Line Conversion to 138 kV | Courtney Creek | Yucca Drive |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6901 |  | 2023-12-15 | 69 | Tier 3 |  |  |  | 1202, 1238, 1239, 11204, 11236, 11262, 1009, 1015, 1203, 1240, 1241, 1242, 11242, 1204, 11246, 11258, 60792 | Y | 64552 | 62693
3155 | Elkton 345/138 kV autotransformer | Replace existing autotransformer | Elkton | Elkton |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6902 |  | 2024-05-15 | 345 | Tier 3 |  |  |  | 3105, 3106, 29150 | Y | 10501 | 3155
5479 | Trinidad - Tri Corner 345 kV Double-Circuit Line | Upgrade existing DCKT line | Trinidad Sw. Sta | TriCorner/Watermill |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6903 |  | 2024-05-15 | 345 | Tier 3 |  |  |  | 2432, 3123, 3124 | Y | 13184 | 5479
5981 | Shamburger North 345/138 kV Sw. Sta. | Establish Shamburger North 345/138 kV Sw. Sta. | Shamburger North | Shamburger North |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6904 |  | 2024-05-15 | 345 | Tier 3 |  |  |  | 3217, 3223, 3226, 2478, 3103, 3201, 3206 | Y | 13696 | 5981
6304 | Shamburger North - Shamburger 345 kV Line | Upgrade existing 345 kV Line | Shamburger North | Shamburger |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6905 |  | 2024-05-28 | 345 | Tier 3 |  |  |  | 3103, 3223 | Y | 14033 | 6304
5436 | Morgan Creek - McDonald 138 kV Line | Upgrade existing line | Morgan Creek | McDonald Rd |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6906 |  | 2025-05-15 | 138 | Tier 3 |  |  |  | 1032, 1333 | Y | 13139 | 5436
2489 | Forney Sw. Sta. Second 600 MVA, 345/138 kV Autotransformer | Add second 345/138 autotransformer | Forney Sw. Sta. |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6907 |  | 2027-05-15 | 345 | Tier 3 | 2008-06-01 | 2008-07-01 |  | 2437, 2438 | Y | 9769 | 2489
4834 | Cresson - Rocky Creek 138 kV Line | Construct new line | Cresson | Rocky Creek |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6908 |  | 2027-05-15 | 138 | Tier 2 |  |  |  | 1881, 2202 | Y | 12436 | 4834
5522 | Lake Hubbard 345/138 kV Switching Station | Construct new 345/138 kV switching station | Lake Hubbard |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6909 |  | 2027-05-15 | 345 | Tier 3 |  |  |  | 12455, 12456, 2401, 2402, 2455 | Y | 13249 | 5522
5525 | Forney - Lake Hubbard 345 kV Line | Construct new 345 kV line | Forney | Lake Hubbard |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6910 |  | 2027-05-15 | 345 | Tier 2 | N/A | N/A | N/A | 2455, 2467 | Y | 13252 | 5525
5526 | Forney 345 kV Switching Station | Reconstruct existing 345 kV switching station | Forney |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6911 |  | 2027-05-15 | 345 | Tier 3 | N/A | N/A | N/A | 2467, 2433, 2437, 2470, 2478, 150189, 2438, 12438 | Y | 49916 | 5526
6287 | Sherry Sw. - Webb/Kennedale 345 kV DCKT Line | Upgrade the existing 345 kV Line | Sherry | Webb/Kennedale |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6912 |  | 2027-05-15 | 345 | Tier 3 |  |  |  | 1911, 1918, 1930, 1929, 1932, 1934 | Y | 14016 | 6287
5524 | Royse South 345/138 kV Switching Station | Establish new 345/138 kV switching station | Royse | Forney |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6913 |  | 2027-05-15 12:00 | 345 | Tier 3 | N/A | N/A | N/A | 2469, 2470, 12471, 2437, 2467, 2471, 2478, 2702, 2472, 2474, 2710, 3223, 12702 | Y | 49918 | 5524
RPG Projects With ISD Changes
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Original Projected In-Service Date (Month/Yr) | New Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number

## Recently Approved RPG Projects
Date Last Updated: | 2022-11-22 |  | Back
Status | Final
RPG Project ID | RPG Project Name | TDSP | Approve Date
21RPG012 | Andrews North – Mustang – Paul Davis Tap 138-kV Line Section | ONCOR | 2021
21RPG016 | TH Wharton - White Oak 138-kV Conversion Project | CNP | 2021
21RPG002 | Port Lavaca Area Improvement Project | AEPSC | 2021
21RPG017 | Lower Rio Grand Valley (LRGV) System Enhancement Project | STEC and AEPSC | 2021
21RPG019 | Howard Road 345/138-kV Switching Station Project | CPS | 2021
21RPG020 | Galena Park Area 138-kV Conversion Project | CNP | 2021
21RPG022 | 138 kV Marshall Ford - Rutherford Line Rebuild | PEC | 2022
21RPG024 | Tungsten 138/69 kV Station Transmission Project | AEPSC | 2022
21RPG002 | Port Lavaca Area Improvement Project | STEC and AEPSC | 2022
22RPG013 | Red Oak Upgrades Project | ONCOR | 2022
20RPG019 | Nacogdoches Southeast Switch – Redland Switch – Lufkin Switch 345 kV Loop Project | ONCOR | 2022
22RPG003 | Oncor Roanoke Area Upgrades | ONCOR | 2022
22RPG006 | Consavvy 345/138 kV Switch Project | Oncor | 2022
22RPG010 | Bearkat – North McCamey – Sand Lake 345-kV Transmission Line Addition Project | LCRA TSC/Oncor/WETT | 2022
22RPG027 | Oncor and LCRA TSC East Hutto Area 345/138 kV Project | Oncor/LCRA TSC | 2022

## Model Updates & Corrections
Date Last Updated: | 2022-10-06 | Back
Status | Final
Model Corrections/Updates Made to the 2022 RTP Cases
Transmission Changes | TO | [5 empty] | Comments
|  | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM
Interconnected the Mirage unit (111161) so that it is no longer islanded | CNP | X | X | X | X | X | Based on CNP feedback
Updated branch rating and/or impedance values for the following branches: 9287 - 9328, 9129 - 9227, 9287 - 9148, 9147 - 9148, 7202 - 9147) | AEN | X | X | X | X | X | Based on AEN feedback
Added CNP Tier 4 MOD project 66046 | CNP | X | X | X | X | X | MOD ID 66046, based on CNP feedback
Added CNP Tier 4 MOD project 66050 | CNP | X | X | X | X | X | MOD ID 66050, based on CNP feedback
Added CNP Tier 4 MOD project 66063 | CNP | X | X | X | X | X | MOD ID 66063, based on CNP feedback
Applied IHS new load related topology | Multiple | X | X | X | X | X | Based on IHS new load interconnection information provided by the TSPs
Deleted islanded bus 1229 and moved load to bus 11229 | Oncor | X | X | X | X | X | Based on Oncor feedback
Corrected the ratings of the line from 44630 - 40172 ckt 66. | CNP | X | X | X | X | X | Based on CNP feedback
Updated Friess Ranch to Sonora 69 kV transmission line parameter and ratings | AEP | X | X | X | X | X | Based on AEP feedback
Added in McCree area Improvement project-approved RPG project 2 years ago, not yet incorporated into SSWG cases | Garland | X | X | X | X | X | Approved RPG project
Updated the ratings of the line from POES (902) to Spence (981) | Oncor | X | X | X | X | X | based on operations/NMMS model
Added TNMP Tier 4 MOD project 68673 that upgrades the 138-kV line from 1074 - 37900. | TNMP | X | X | X | X | X | MOD ID 68673, based on TNMP feedback
Added the TNMP Tier 4 MOD Project 65663 that adds a 138-kV line from 38091-38124. | TNMP | X | X | X | X | X | MOD ID 65663, based on TNMP feedback
Added the TNMP Tier 4 MOD project 65661 that upgrades the 138-kV line from 37981 to 38001. | TNMP | X | X | X | X | X | MOD ID 65661 based on TNMP feedback
Added the TNMP Tier 4 Fishhook project (MOD 65659) that adds the 138-kV Fishhook bus and taps that bus into several nearby 138-kV lines. | TNMP | X | X | X | X | X | MOD ID 65659 based on TNMP feedback
Updated the ratings of the line from WAP POI 44015 to GenWAP 49215 | N/A | X | X | X | X | X | based on operations/NMMS model
Added the CNP Tier 4 MOD project 66017B to upgrade the line from 44762 Wchase to 47072 Dunval | CNP | X | X | X | X | X | MOD 66017B
Added the CNP tier 4 MOD project 57251B to upgrade the line from 45880 Hockly to 45886 Hockly to 44840 StoneLake | CNP | X | X | X | X | X | MOD 57251B
Added Tier 4 TNMP MOD Project 66111 that upgrades the 138-kV line from 38330 - 38340. | TNMP | X | X | X | X | X | MOD ID 66111, based on TNMP feedback
Added Tier 4 TNMP MOD Project 66077 that upgrades both circuits of the 138-kV line from 38091 - 38145. | TNMP | X | X | X | X | X | MOD ID 66077, based on TNMP feedback
Added the 138-kV line from Johnson Draw to Sky West (11344 - 71210) to match the Flat Iron to Barr Ranch RPG acceptance letter. | Oncor | X | X | X | X | X | Based on Oncor feedback and RPG documents
Corrected the rating of the 138-kV AEP line from Rio Pecos to Lynx to 558/660/660 based on AEP feedback. | AEP | X | X | X | X | X | Based on AEP feedback
Added cap bank at Portilla station (8924) | AEP | X | X | X | X | X | MOD 61394
Applied rating upgrade for Hamwolf (5187)-Med_Ctr (5300) and Medinabs (5305) - 36th_St (5427) | CPS |  | X | X | X | X | Part of recently approved RPG project 21RPG019
San Miguel transformer tierary winding reactor (5908) rating correction | STEC | X | X | X | X | X | Based on STEP feedback
Disconncet line HHGT (170246) to Omega (170251) | LCRA | X | X | X | X | X | Based on LCRA feedback
Upgrade tier 4 138 kV line from Freeway Park 38820 to Dickinson 38850 | TNMP | X | X | X | X | X | MOD 66120
Updated the parameters of the 138-kv radial line from Blackland RC (6886) to West Munson Sub POD (6888) | Rayburn | X | X | X | X | X | Based on Rayburn feedback
Transformer Changes | TO | [5 empty] | Comments
|  | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM
Updated White Mesa transformer from 134651/134654 to 134653/134654 | LCRA | x | x | x | x | x | Based on RARF data
Updated White Mesa transformer from 134651/134655 to 134653/134655 | LCRA | x | x | x | x | x | Based on RARF data
Corrected the 0 MVA ratings for the following transformers with ratings provided in their RARFs: (112419 - 112411 - 112412), (112419 - 112415 - 112416), (112419 - 112417 - 112418), (112419 - 112413 - 112414) | CNP | x | x | x | x | x | Based on RARF data
Generation Changes | TO/GO | [5 empty] | Comments
|  | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM
Updated Rodeo Solar 135501 (19INR0103) to be offline | Oncor | X | X | X | X | X | Inactive status
Updated the Unit ID for the following units to better represent their status and align with the latest SSWG cases: (111142 PE -> PG, 110381 PE -> PG, 110019 BS -> N5, 110041 BS -> N7) | CNP/Exxon & Formosa | X | X | X | X | X | Based on feedback from the Resource Entities and ERCOT Operations
Updated LPL generators status and MW capacity | LPL | X | X | X | X | X | Based on LPL feedback
Updated Pmax for Chamon 2 units (#112331 and #112332) | CNP | X | X | X | X | X | Based on latest RARF
Updated Pmax for Victport units (#112311 and #112312) | AEP | X | X | X | X | X | Based on latest RARF
Updated air Products unit to be connected to a 138 kV bus 38585 (was 69 kV bus 112011 before) | TNMP | X | X | X | X | X | Based on TNMP feedback
Load Changes | TO | [5 empty] | Comments
|  | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM
Added CNP load updates based on load comparison with last year's SSWG cases | CNP | X | X | X | X | X | Based on CNP feedback
Added Bryan load updates based on load comparison with last year's SSWG cases | Bryan |  | X | X |  |  | Based on Bryan feedback
Applied IHS load forecast | Multiple | X | X | X | X | X | Based on IHS load forecast
Added the self served load at the Air Products generation site | TNMP | X | X | X | X | X | Based on TNMP feedback
Modified MW and Mvar values for load at bus 38146 | TNMP | X | X | X | X | X | Based on TNMP feedback
Bus Voltage Changes | TO | [5 empty] | Comments
|  | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM
Updated upper voltage limit at bus 3584 to 1.05 pu | Oncor | X | X | X | X | X | Based on Oncor feedback
Reactive Device Changes | TO | [5 empty] | Comments
|  | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM
Added a 100 Mvar reactor at Latimer (68008) to represent the existing reactor at that bus in operations | LST | X | X | X | X | X | Based on the operations model and feedback from LST
Corrected the number of reactor steps in the shunt at Tule Canyon (23914) by adding two more -50 Mvar reactor steps. | Oncor | X | X | X | X | X | Based on feedback from Oncor
Corrected the Mvar value of the shunt at bus 23930 from -100 Mvar to -75 Mvar. | Oncor | X | X | X | X | X | Based on feedback from Oncor
Phase Shifters Changes | TO | [5 empty] | Comments
|  | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM
Synchronous Condensers Changes | TO | [5 empty] | Comments
|  | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM
FACTS Device Changes | TO | [5 empty] | Comments
|  | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM
Device at Cottonwood Customer Substation (bu 38097) is not a FACTS device but is a discrete voltage controlled capacitor bank | TNMP | x | x | x | x | x | Confirmed by TNMP
Device at Cedarvale Customer Substation (bus 38146) is not a FACTS device but is a discrete voltage controlled capacitor bank | TNMP | x | x | x | x | x | Confirmed by TNMP
Device at Lonestar Customer Substation (bus 38191) is not a FACTS device but is a discrete voltage controlled capacitor bank | TNMP | x | x | x | x | x | Confirmed by TNMP
Device at GIBBONS CREEK (Bus 967 V1 )should be switched reactor, not FACTS device | TMPA | x | x | x | x | x | Confirmed by TMPA
Device at GIBBONS CREEK (bus 968 V2) should be switched reactor, not FACTS device | TMPA | x | x | x | x | x | Confirmed by TMPA
FACTS device at Tulsyncon (bus 23917) was removed due to a modeling error | ONCOR | x | x | x | x | x | Confirmed by ONCOR
FACTS device at North Brady (bus 60201) was removed due to retirement | AEP | x | x | x | x | x | Confirmed by AEP
FACTS device at Military Highway (bus 80003) was removed due to retirement | AEP | x | x | x | x | x | Confirmed by AEP
Modified the capacity for FACTS device at Tesla (bus 60502) | AEP | x | x | x | x | x | Data provided by AEP
Modified the capacity for FACTS device at Tesla (bus 60503) | AEP | x | x | x | x | x | Data provided by AEP
Modified the capacity for FACTS device at Laredo (bus 80012) | AEP | x | x | x | x | x | Data provided by AEP
Modified the capacity for FACTS device at Hamilton Road (bus 80479) | AEP | x | x | x | x | x | Data provided by AEP
Modified the capacity for FACTS device at Hamilton Road (bus 80480) | AEP | x | x | x | x | x | Data provided by AEP
Changed the limits of the Parker Switch (bus 11437) FACTS device to 0 | ONCOR | x | x | x | x | x | Confirmed by ONCOR
Changed the limits of the Renner Switch (bus 12357) FACTS device to 0 | ONCOR | x | x | x | x | x | Confirmed by ONCOR
Changed the limits of the 12359 (Renner Switch) FACTS device to 0 | ONCOR | x | x | x | x | x | Confirmed by ONCOR
Changed the limits of the Parkdale Switch (bus 12440) FACTS device to 0 | ONCOR | x | x | x | x | x | Confirmed by ONCOR
Changed the limits of the Parkdale Switch (bus 12449) FACTS device to 0 | ONCOR | x | x | x | x | x | Confirmed by ONCOR

## Transmission & Gen Outages
Date Last Updated: | 2022-09-14 |  | Back
Status | Final
Case
Outaged Elements | Outage Description | Associated TO/RE | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM | Notes
Known outages collected by ERCOT from TSPs and Resource Entities were incorporated based on the TSP and ERCOT technical rationale into the known outages impact studies.

## Temp. for Dynamic Ratings
Date Last Updated: | 2022-01-04 | Back
Status | Final
Weather Zone | 90th Percentile Temperature (degree F)
Coast | 100
East | 105
Far West | 110
North Central | 110
North | 110
South Central | 105
South | 105
West | 110

## Gen Add. Ret. and Mothball
Date Last Updated: | 2022-04-28 |  | Back
Status | Final
Based on generators met PG Section 6.9 requirements (1)9b) through 1(d) by 2/1/2022
New generators that met PG 6.9 requirements
GINR Reference Number | Project Name | County | Projected COD | Fuel | MW For Grid | Meets Section 6.9 Requirements (1)(b) through (1)(d) | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM | Comments
19INR0073 | McLean (Shakes) Solar | Zavala | 2022-11-09 | Solar | 206 | Y | Y | Y | Y | Y | Y
19INR0131 | Rowland Solar 1 | Fort Bend | 2022-08-16 | Solar | 101.75 | Y | Y | Y | Y | Y | Y
20INR0026 | Longbow Solar | Brazoria | 2022-08-15 | Solar | 78.15 | Y | Y | Y | Y | Y | Y
20INR0097 | El Sauz Ranch | Willacy | 2022-10-01 | Wind | 301.5 | Y | Y | Y | Y | Y | Y
20INR0205 | Roseland Solar | Falls | 2023-02-06 | Solar | 254 | Y | Y | Y | Y | Y | Y
20INR0230 | Markum Solar | McLennan | 2024-02-05 | Solar | 161 | Y | Y | Y | Y | Y | Y
20INR0241 | Crowded Star Solar | Jones | 2024-10-03 | Solar | 217.6 | Y | Y | Y | Y | Y | Y
20INR0268 | Pyron BESS II | Nolan | 2022-07-30 | Other | 30.2 | Y | Y | Y | Y | Y | Y
20INR0290 | River Valley Storage 1 | Williamson | 2022-11-01 | Other | 51.5 | Y | Y | Y | Y | Y | Y
20INR0293 | River Valley Storage 2 | Williamson | 2022-11-01 | Other | 51.5 | Y | Y | Y | Y | Y | Y
21INR0281 | Byrd Ranch Energy Storage Plant | Brazoria | 2022-08-01 | Other | 50.6 | Y | Y | Y | Y | Y | Y
21INR0375 | Grizzly Ridge Solar | Hamilton | 2022-08-26 | Solar | 101.68 | Y | Y | Y | Y | Y | Y
21INR0479 | Endurance Park Storage | Scurry | 2022-11-01 | Other | 51.5 | Y | Y | Y | Y | Y | Y
21INR0493 | Ellis Solar | Ellis | 2022-06-30 | Solar | 81.31 | Y | Y | Y | Y | Y | Y
21INR0497 | Swoose II | Ward | 2022-04-27 | Other | 100.98 | Y | Y | Y | Y | Y | Y
21INR0512 | Colorado Bend I Expansion | Wharton | 2022-11-01 | Gas | 78 | Y | Y | Y | Y | Y | Y
21INR0521 | White Mesa 2 Wind | Crockett | 2022-03-14 | Wind | 348 | Y | Y | Y | Y | Y | Y
21INR0541 | Bastrop Energy Center AGP repower Phase I | Bastrop | 2022-04-30 | Gas | 594 | Y | Y | Y | Y | Y | Y
22INR0280 | Roseland Storage | Falls | 2022-12-05 | Other | 51.63 | Y | Y | Y | Y | Y | Y
22INR0322 | BRP Paleo BESS | Hale | 2022-12-01 | Other | 202.36 | Y | Y | Y | Y | Y | Y
22INR0325 | BRP Dickens BESS | Dickens | 2022-12-01 | Other | 202.33 | Y | Y | Y | Y | Y | Y
22INR0369 | Beachwood Power Station (Mark One) | Brazoria | 2022-06-25 | Gas | 363 | Y | Y | Y | Y | Y | Y
22INR0372 | BRP Hydra BESS | Pecos | 2022-12-01 | Other | 202.31 | Y | Y | Y | Y | Y | Y
22INR0436 | Noble Storage | Denton | 2022-08-01 | Other | 127 | Y | Y | Y | Y | Y | Y
22INR0482 | Rowland Solar II | Fort Bend | 2023-04-15 | Solar | 202.81 | Y | Y | Y | Y | Y | Y
22INR0506 | Roseland Solar II | Falls | 2023-02-06 | Solar | 254 | Y | Y | Y | Y | Y | Y
22INR0533 | Temple Generation I Repower | Bell | 2022-06-15 | Gas | 769 | Y | Y | Y | Y | Y | Y
22INR0535 | Bastrop Energy Center AGP repower Phase II | Bastrop | 2022-04-30 | Gas | 615 | Y | Y | Y | Y | Y | Y
23INR0019 | Blue Jay BESS | Grimes | 2022-11-17 | Other | 51.63 | Y | Y | Y | Y | Y | Y
23INR0027 | Cachena Solar SLF | Wilson | 2024-06-01 | Solar | 440 | Y | Y | Y | Y | Y | Y
23INR0180 | Jackalope Solar | San Patricio | 2023-07-01 | Solar | 156.4 | Y | Y | Y | Y | Y | Y
22INR0326 | Inertia Wind | Haskell | 2022-12-31 | Wind | 350 | Y | Y | Y | Y | Y | Y
22INR0328 | Inertia BESS | Haskell | 2022-12-31 | Other | 121.45 | Y | Y | Y | Y | Y | Y
22INR0374 | Inertia Solar | Haskell | 2023-12-31 | Solar | 258.35 | Y | Y | Y | Y | Y | Y
22INR0375 | Inertia BESS 2 | Haskell | 2022-12-31 | Other | 100.77 | Y | Y | Y | Y | Y | Y
19INR0117 | Roadrunner Crossing Wind | EastLand | 2022-12-15 | Wind | 200 | Y | Y | Y | Y | Y | Y
20INR0236 | Old Hickory Solar | Jackson | 2023-05-31 | Solar | 206 | Y | Y | Y | Y | Y | Y
Retired Units
Unit Name | MW For Grid | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM | Comments
DECKER_DPG2 | 420 | X | X | X | X | X | NSO posted
Generation Resources Unavailable in Planning Studies Prior to NSO
Unit Name | MW For Grid | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM | Comments
COL_COLETOG1 | 655 |  |  |  | X | X | https://mis.ercot.com/secure/data-products/grid/generation?id=PG3-1411-M
BRAUNIG_VHB1 | 217 |  | X | X | X | X
BRAUNIG_VHB2 | 230 |  | X | X | X | X
BRAUNIG_VHB3 | 412 |  | X | X | X | X
CALAVER_OWS1 | 420 |  |  |  | X | X
Mothballed Units
Unit Name | MW For Grid | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM | Comments
OLINGR_OLING_1 | 78 | X | X | X | X | X | From CDR and NSO posted
CALAVERS_JTD1_M | 420 | X | X | X | X | X | From CDR and NSO posted
CALAVERS_JTD2_M | 420 | X | X | X | X | X | From CDR and NSO posted
WAP_GT2 | 71 | X | X | X | X | X | NSO posted
Seasonal Mothballed Units (Offline in the 2024 Min case only)
Unit Name | MW For Grid | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM | Comments
LGE_LGE_GT1 | 145 | X |  | X | X | X | From posted NSO (AS OF 1/1/2022, AVAILABLE 1/1 THROUGH 9/30)
LGE_LGE_GT2 | 145 | X |  | X | X | X | From posted NSO (AS OF 1/1/2022, AVAILABLE 1/1 THROUGH 9/30)
LGE_LGE_STG | 75 | X |  | X | X | X | From posted NSO (AS OF 1/1/2022, AVAILABLE 1/1 THROUGH 9/30)
Planned Units Removed Due to Project Cancellation
Unit Name | MW For Grid | 2024 SUM | 2025 MIN | 2025 SUM | 2027 SUM | 2028 SUM | Comments
NOTES: Simple model Settlement Only Distributed Generators (SODGs) were added to reflect those currently operational. Battery models were also added to reflect those currently in the Operations model.

## Renewable Generation Dispatch
Date Last Updated: | 2022-04-15 |  | Back
Status | Final
Solar
Information obtained from the spreadsheet "CDR_Summer_PeakAveSolarCapacityPercentages_11-23-2021" posted on the ERCOT website under Resource Adequacy. Note: Solar units are offline in the Min case.
* SOLARPEAKPCT Values | 81%
* The methodology for calculating SOLARPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See:http://www.ercot.com/content/wcm/current_guides/53528/03-090118_Nodal.docx
Wind
Information obtained from the spreadsheet "CDR_Summer_PeakAveWindCapacityPercentages_11_23-2020" posted on the ERCOT website under Resource Adequacy.
Outside Study Region
WINDPEAKPCT Values *
Summer, Coastal | Summer, Panhandle | Summer, Other
57% | 30% | 20%
* The methodology for calculating WINDPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See:http://www.ercot.com/content/wcm/current_guides/53528/03-090118_Nodal.docx
Inside Study Region
Summer, Coastal | Summer, Panhandle | Summer, Other
37% | 13% | 9%
Inside and Outside Study Region
Min Case, Coastal | Min Case, Panhandle | Min Case, Other
27% | 54% | 45%
Hydro
Unit specific generation MW dispatch modeled using CDR methodology which is based on historical Settlements HSL dispatch levels during the top 20 load hours of the last three years. Note: All Hydro units are offline in the Min case.
AMI_AMISTAG1 (H1) | 27
AMI_AMISTAG2 (H2) | 27.3
AUS_AUSTING1 (H2) | 8.1
AUS_AUSTING1 (H1) | 8.4
BUC_BUCHANG1 (H1) | 17.6
BUC_BUCHANG2 (H2) | 17.6
BUC_BUCHANG3 (H3) | 17.9
CAN_CANYHYG1 (H1) | 0
CAN_CANYHYG1 (H2) | 0
DND_DENISOG1 (H1) | 44
DND_DENISOG2 (H2) | 44
EA_EAGLE_HY1 (H3) | 0
EA_EAGLE_HY1 (H2) | 0
EA_EAGLE_HY1 (H1) | 0
FAL_FALCONG1 (H1) | 7.0986
FAL_FALCONG2 (H2) | 6.8819
FAL_FALCONG3 (H3) | 7.614
INKS_INKS_G1 (H1) | 13.4
MAR_MARBFAG1 (H1) | 20.3033
MAR_MARBFAG2 (H2) | 19.9033
MAR_MARSFOG1 (H1) | 35.0667
MAR_MARSFOG2 (H2) | 35.7967
MAR_MARSFOG3 (H3) | 35.7333
WIR_WIRTZ_G1 (H1) | 28.7933
WIR_WIRTZ_G2 (H2) | 29.54
WND_WHITNEY1 (H1) | 20.7433
WND_WHITNEY2 (H2) | 20.7433

## Switchable Generation
Date Last Updated: | 2022-04-28 |  | Back
Status | Final
Operational Resources Unavailable to ERCOT (Switchable)
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
ANTELOPE IC 1 | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54
ANTELOPE IC 2 | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54
ANTELOPE IC 3 | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2017 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54 | -54
ELK STATION CTG 1 | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190
ELK STATION CTG 2 | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2017 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190 | -190
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  |  |  |  | -542 | -542 | -542 | -542 | -542 | -542 | -542 | -542 | -542 | -542

## DC Tie Modeling & Dispatch
Date Last Updated: | 2022-04-15 |  | Back
Status | Final
Reliability Analysis
DC Tie Dispatch - Summer Peak Conditions (MW)
DC_E | 600 | Import
DC_N | 220 | Import
DC_L* | 0
DC_R* | 0
DC Tie Dispatch - Minimum Load Conditions (MW)
DC_E | 0
DC_N | 0
DC_L* | 0
DC_R* | 0
* In the events that thermal overloads are resolved by curtialing the DC Tie exports, the events and the curtailed amounts will be documented.

## Reserve Requirement
Date Last Updated: | 2022-01-04 | Back
Status | Final
Reliabity Cases | 3000 MW
The reserve requirements used in the reliability models account for the outage of ERCOT's two largest units as well as the increased losses observed during such an G-1 & N-1 outage.

## Fuel Price Assumptions
Date Last Updated: | 2022-04-12 |  | Back
Status | Final
Source
Natural Gas Price Forecast ($/MMBtu)
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average
2022 | 4.1489 | 3.9769 | 3.7077 | 3.7781 | 3.8466 | 3.9253 | 3.8145 | 3.8347 | 3.8513 | 4.0474 | 4.0516 | 4.2487 | 3.936
2023 | 3.8381 | 3.679 | 3.43 | 3.4951 | 3.5584 | 3.6313 | 3.5288 | 3.5475 | 3.5628 | 3.7442 | 3.7481 | 3.9305 | 3.6412
2024 | 3.5673 | 3.4193 | 3.1879 | 3.2484 | 3.3073 | 3.375 | 3.2798 | 3.2971 | 3.3114 | 3.48 | 3.4836 | 3.6531 | 3.3842
2025 | 3.4519 | 3.3087 | 3.0848 | 3.1433 | 3.2003 | 3.2658 | 3.1737 | 3.1905 | 3.2043 | 3.3674 | 3.3709 | 3.5349 | 3.2747
2026 | 3.5098 | 3.3642 | 3.1365 | 3.1961 | 3.254 | 3.3206 | 3.2269 | 3.244 | 3.258 | 3.4239 | 3.4275 | 3.5942 | 3.3296
2027 | 3.7165 | 3.5624 | 3.3213 | 3.3843 | 3.4456 | 3.5162 | 3.4169 | 3.435 | 3.4499 | 3.6255 | 3.6293 | 3.8059 | 3.5257
2028 | 4.0267 | 3.8597 | 3.5985 | 3.6668 | 3.7332 | 3.8096 | 3.7021 | 3.7217 | 3.7378 | 3.9281 | 3.9322 | 4.1235 | 3.82

## Reliability Case-Load Forecast
Date Last Updated | 2022-11-05 | Back
Status | Final
SSWG Load– Based on 21 SSWG cases posted on 10/22/2021 less self-serve load (MW)
Year | Coast | East | Far West | North | North Central | South Central | South | West | NCP Total
2024 | 25514 | 3234 | 9160 | 3272 | 29197 | 15264 | 7508 | 2391 | 95540
2025 | 25610 | 3268 | 9406 | 3287 | 29776 | 15627 | 7648 | 2413 | 97035
2027 | 25907 | 3347 | 9756 | 3372 | 30978 | 16105 | 7859 | 2469 | 99793
2028 | 25939 | 3380 | 9936 | 3401 | 31547 | 16354 | 7969 | 2499 | 101025
ERCOT 90th percentile Load Forecast– less losses for RTP (MW)
Year | Coast | East | Far West | North | North Central | South Central | South | West | NCP Total
2024 | 22269 | 2742 | 5985 | 2304 | 27068 | 13754 | 7349 | 2073 | 83544
2025 | 22467 | 2757 | 6369 | 2316 | 27379 | 13908 | 7443 | 2089 | 84728
2027 | 22863 | 2789 | 6928 | 2349 | 27974 | 14197 | 7631 | 2122 | 86853
2028 | 23052 | 2805 | 7102 | 2365 | 28247 | 14330 | 7721 | 2139 | 87761
2022 RTP load level with self-served load (MW) (based on on 7.5% boundary threshold, ERCOT load review results, and the incorporation of the IHS Markit study Permian Basin load forecast and rooftop PV growth forecast contribution)
Year | Coast | East | Far West | North | North Central | South Central | South | West | Total
2024 | 28128 | 2974 | 10751 | 4784 | 29704 | 15766 | 7982 | 2643 | 102732
2025 | 28301 | 2990 | 11229 | 4790 | 29994 | 16187 | 8105 | 2689 | 104285
2027 | 28693 | 3016 | 11990 | 4812 | 30550 | 16337 | 8280 | 2738 | 106416
2028 | 28881 | 3030 | 12241 | 4821 | 30768 | 16921 | 8372 | 2785 | 107819
2022 RTP load level with self-served load for Off-Peak Case (MW) (based on 2025 SSWG Min Case and adjusted with ERCOT load review results)
Year | Coast | East | Far West | North | North Central | South Central | South | West | Total
2025 | 15197 | 1164 | 7542 | 3504 | 10107 | 6742 | 4483 | 1463 | 50202

## Sensitivity Analysis
Date Last Updated: | 2022-11-30 | Back
Status | Final
For sensitivity 1, the wind and solar output values below reflect their assumed output prior to any redispatch to alleviate transmission constraints. For sensitivity 2, the wind and solar output values below reflect their assumed output after the needed curtailment to maintain system critical intertia and stability limits.
Sensitivity 1: | Winter Coincident Peak Load
Year | ERCOT Load (MW) | DC Tie Export* (MW) | Wind Output (MW) |  |  | Solar Output (MW) | Total Renewable Output (MW)
|  |  | Coastal | Panhandle | Other
2024 | 88992 | -820 | 774 | 2997 | 14345 | 858 | 18974
2027 | 93124 | -820 | 778 | 2997 | 15071 | 901 | 19747
Sensitivity 2: | High Renewable Light Load
Case | ERCOT Load (MW) | DC Tie Export* (MW) | Wind Output (MW) |  |  | Solar Output (MW) | Total Renewable Output (MW)
|  |  | Coastal | Panhandle | Other
2025 | 52452 | 100 | 3189 | 19666 | 3484 | 15762 | 42101
* negative sign indicating DC tie import.