## Slide 1
ROS | January 5th, 2022
Luis Hinojosa
ERCOT
Balancing Operations Planning
Energy Storage Resource – Common Operational Performance Issues

## Slide 2: Overview
There is a steady growth in the amount of Energy Storage Resources (ESRs) that have interconnected into the ERCOT Grid.
ERCOT has been monitoring ESR performance in their ability to follow BPs, provide Ancillary Services (AS) (specifically Regulation and Responsive Reserve Service) and maintain State-Of-Charge (SOC) for the AS responsibility being carried.
Through this analysis ERCOT has identified some common issues that affect ESR’s ability to meet the operational performance requirements.
  Details on the underlying cause for these were discussed at the Nov 16, 2022 PDCWG and Nov 18, 2022 WMWG.
  After these discussion, a revised version of the Business Practice Manual – ERCOT and QSE Operations Practices During the Operating Hour was posted on December 21, 2022.
  A high-level summary of the common issues will be shared in the next few slides.

## Slide 3: High-level Summary of Topics Discussed
Below is a list of common issues that have been observed during real-time operations:
  Limited Primary Frequency Response (PFR) or no PFR response when frequency is outside of the dead-band
    Discussed the expectations around PFR response and clarified that PFR response is expected when the frequency responsive headroom/legroom is available regardless of whether the ESR is carrying Ancillary Services (AS) or not
  Insufficient headroom/legroom maintained for the AS Obligation being carried
  Reinforced the need to use Base Points (BP) as an indication of when discharging or charging was acceptable
    In this context, also discussed the need to follow an Updated Desired Base Point (UDBP) like signal when ramping from one BP to the next
  Inappropriate transitions of AS responsibility from discharging to charging side of ESR were observed during an active deployment
    Discussed the operational conditions when transitioning from discharging to charging was not acceptable in case of each AS
  Reinforced the need to provide accurate actual SOC and other related telemetry as SOC is used to account for an ESR’s headroom in PRC and for situational awareness in the control room
  Insufficient amount of SOC preserved when carrying up AS on the discharging side
    Expectations on the amount of SOC that needs to be preserved when AS is carried on the discharging side of an ESR were discussed

## Slide 4: Summary & Next Steps
There is a steady growth in the amount of Energy Storage Resources (ESRs) that have interconnected into the ERCOT Grid.
ERCOT has identified several issues with ESR performance in their ability to follow BPs/Expected Gen, provide AS including inappropriate transitions of up AS responsibilities between discharging and charging sides and maintain state-of-charge for the AS responsibility being carried.
ERCOT has updated the Business Practice Manual – ERCOT and QSE Operations Practices During the Operating Hour to include or clarify operational expectations as applicable to ESRs.
ERCOT will continue to conduct active outreach with QSEs as issues are identified to ensure that these get resolved in a timely manner.