## Slide 1
December 2022 Cold Weather Operations:
Preliminary Observations
Dan Woodfin
Vice President, System Operations
TAC
ERCOT Public
January 24, 2023

## Slide 2: Advance Notifications
Date Time | Notice
12/16/2022 8:59 | OCN issued for the predicted extreme cold weather event for the ERCOT Region Thursday morning, December 22, 2022 through Monday, December 26, 2022.
12/19/2022 13:26 | Advisory issued for the predicted extreme cold weather event for the ERCOT Region Thursday morning, December 22, 2022 through Monday, December 26, 2022.
12/21/2022 10:00 | Watch issued for the predicted extreme cold weather event for the ERCOT Region Thursday morning, December 22, 2022 through Monday, December 26, 2022.
12/25/2022 11:52 | ERCOT cancelled the following notice: At 10:00, Watch issued for the predicted extreme cold weather event for the ERCOT Region Thursday morning, December 22, 2022 through Monday, December 26, 2022.

## Slide 3: Weather
Minimum daily temperatures don’t tell the whole story, but are one indicator of severity
Winds were also very strong

## Slide 4: Load Forecast
Load Forecasts were too low going into event
  Cold weather intrusion was deeper and quicker than the national weather models were forecasting
  Load forecasting models overplayed the reduction in demand due to the holiday
  Lack of historic load data without loadshed for temperatures this cold for the load forecast models to reference
Many other system operators across the eastern US had similar forecast errors
The under-forecast had no impact on reliability because ERCOT intentionally prepared for higher demand than what the forecast models were projecting

## Slide 5: Wind and Solar Forecast
 | Wind forecast (Dec. 22-25, 2022) | Wind forecast (Dec. 2022) | Solar forecast (Dec. 22-25, 2022) | Solar forecast (Dec. 2022)
Day-ahead Forecast Performance (MAPE) | 5.07% | 3.6% | 2.72% | 3.23%
1-hour-ahead Forecast Performance (MAPE) | 2.83% | 1.9% | 2.55% | 2.53%
On Thursday 12/22, ERCOT used the most conservative solar forecast and switched to the most conservative wind forecast in the afternoon, in advance of the cold weather and high load
High winds on Thursday 12/22 followed by a down ramp and low winds on 12/23-12/24 was predicted before the cold front arrived

## Slide 6: Supply vs. Demand 12/22-12/24
Thu 12/22
Fri 12/23
Sat 12/24
Chart: 
Thermal Unit Outages at top of hour in OS as of 1/6/2023 10:00

## Slide 7: Supply vs. Demand 12/22-12/24
Thu 12/22
Fri 12/23
Sat 12/24
Chart: 
Load – 73,658 MW
Wind – 23,253 MW
Solar – 0 MW
Thermal Outages – 6,425 MW
Thermal Unit Outages at top of hour in OS as of 1/6/2023 10:00

## Slide 8: Supply vs. Demand 12/22-12/24
Thu 12/22
Fri 12/23
Sat 12/24
Chart: 
Load – 73,910 MW
Wind – 10,304 MW
Solar – 2,353 MW
Thermal Outages – 14,204 MW
Thermal Unit Outages at top of hour in OS as of 1/6/2023 10:00

## Slide 9: Supply vs. Demand 12/22-12/24
Thu 12/22
Fri 12/23
Sat 12/24
Chart: 
Load – 67,979 MW
Wind – 3,083 MW
Solar – 0 MW
Thermal Outages – 10,593
Thermal Unit Outages at top of hour in OS as of 1/6/2023 10:00

## Slide 10: Real-time Pricing

## Slide 11: Generation Outages - Preliminary
Wind and Solar are at nameplate MW; actual reduction in output due to outage/derate was less
ERCOT has sent RFIs to generators to gather more information about outage causes
Weatherization Inspection team is following up with units that had forced outages that began during this time period

## Slide 12: System-Wide LFL Consumption
A significant portion of the load associated with known LFLs curtailed during the event in to response market prices.
At its peak, the response from LFLs totaled ~1,280 MW with an additional 75 MW carrying RRS.
Notes: All LFLs known to be in operation (20) curtailed to some extent during this time.
Minimum load from LFLs was ~125 MW (75 RRS, ~50 MW in residual power consumption from idle datacenters)

## Slide 13: Energy Storage
Notes: This chart shows the total MW and percent contribution of Ancillary Services with a focus on Regulation Up, Responsive Reserve Service (RRS), and Non-Spin that ESRs were carrying during the week. The trend shows that ESRs carry more percentage of total regulation from hours 16-22. ESRs were carrying roughly 45-55% of total RRS-Primary Frequency Response (PFR) and up to 88% of Regulation Up. On December 22, over peak load hours about 50% of Regulation Up was being carried by ESRs, which allowed more conventional capacity to be available for SCED dispatch.

## Slide 14: Natural Gas Limitations
Typical gas restrictions on units in North Texas and several Operational Flow Orders(OFO) issued to prevent gas flowing beyond contract maximums
  Resulted in some natural gas curtailments and reduction of Generation Resource capacity
Firm Fuel Supply Service(FFSS) used to maintain unit availability with natural gas curtailments
  Dave Maggio will be providing further detail on this
One plant reported that line pressure was fluctuating beyond normal levels on a pipeline in Houston area
  No impact to Generation Resources’ output

## Slide 15: TCEQ Enforcement Discretion and DOE Order
Requests to TCEQ and DOE were made to maximize generation and avoid an Emergency Condition
TCEQ Requests
  12/21/22 10:56a.m. - ERCOT requests enforcement discretion beginning at 6:00 a.m. on 12/22/22
  12/21/22 11:27 a.m. - TCEQ grants enforcement discretion
  12/25/22 11:00 a.m. - ERCOT notifies TCEQ that enforcement discretion is no longer needed and may end at noon on 12/25/22
  12/25/22 12:00 p.m.: TCEQ enforcement Discretion ends
DOE Requests
  12/23/22 11:45 a.m.: ERCOT contacts DOE about likely need for 202(c) order
  12/23/22 12:05 p.m.: ERCOT and DOE meet to discuss need for 202(c) order
  12/23/22 7:06 p.m.: ERCOT submits formal request for 202(c) order
  12/23/22 9:00 p.m.: DOE issues 202(c) order
  DOE Order was not used since ERCOT did not declare an Emergency Condition

## Slide 16
Questions?