## Slide 1
Firm Fuel Supply Service (FFSS) Post-Deployment Report for December ‘22
Dave Maggio
ERCOT
Technical Advisory Committee (TAC)
January 24, ‘23

## Slide 2: Background
This presentation is in response to the requirement under Protocol 3.14.5(8):
  “ERCOT will provide a report to the TAC or its designated subcommittee within 45 days of any FFSS deployments, including the Resources deployed and the reason for the deployments.”
There are additional reports that will be provided later in the year, specifically a report required under 3.14.5(10):
  “On an annual basis after the FFSS season, ERCOT will provide a report separately for the total amounts from Section 6.6.14.1, Firm Fuel Supply Service Fuel Replacement Costs Recovery, and Section 6.6.14.2, Firm Fuel Supply Service Hourly Standby Fee Payment and Fuel Replacement Cost Recovery, to the TAC or its designated subcommittee.”

## Slide 3: Background
Leading up to the cold weather that started on December 22nd, ERCOT began receiving information from Generation Resources and natural gas distributors regarding potential gas restrictions.
  This included information on whether Resources would be able to run without utilizing reserve fuel procured through the FFSS program.
12/21
12/22
12/23
12/24
12/25
12/26
10:00 - Watch issued for forecasted extreme cold weather from 12/22 through 12/26
12:00 - Public notice issued instructing Qualified Scheduling Entities (QSEs) to prepare for potential FFSS deployments
18:38 - First FFSS deployment instructions issued
12:00 - First FFSS deployment starts
~12:00 – Watch and public notice cancelled. Last FFSS deployment ends

## Slide 4: Summary of FFSS Deployments
8 Resources had active FFSS deployments between approximately noon on December 22nd and noon on December 25th.
  The specific period of deployment varied across the different Resources.
The specific Resources deployed, and the timing of those deployments, was based on information from the QSEs, including:
  Was the Resource expecting potential fuel supply limitations;
  Whether the Resource would be able to run without utilizing reserve fuel procured through the FFSS program; and
  Discussions on available amounts of reserve fuel procured through the FFSS program.
Operating Day | Number of Resource Deployed | Total FFSS Deployed in MW (Based on FFSS Awards)
12/22/22 | 4 | 758
12/23/22 | 8 | 949
12/24/22 | 8 | 949
12/25/22 | 2 | 39

## Slide 5: Deployment Details
These deployments were issued through Verbal Dispatch Instruction (VDI) and occurred across multiple VDIs, particularly when they spanned across multiple Operating Days.
Initial Notification Time for Deployment | Resource Name | Deployment Start | Deployment End | Reason
12/21/2022 18:38 | STEAM_STEAM_2 | 12/22/2022 12:00 | 12/24/2022 12:00 | Watch for extreme cold weather
12/21/2022 18:41 | STEAM_STEAM_3 | 12/22/2022 12:00 | 12/24/2022 12:00 | Watch for extreme cold weather
12/21/2022 20:42 | LHSES_UNIT1 | 12/22/2022 12:00 | 12/24/2022 12:00 | Watch for extreme cold weather
12/21/2022 20:45 | LHSES_UNIT2A | 12/22/2022 12:00 | 12/24/2022 12:00 | Watch for extreme cold weather
12/23/2022 12:44 | BRAUNIG_VHB6CT7 | 12/23/2022 13:15 | 12/24/2022 9:28 | Watch for extreme cold weather
12/23/2022 12:44 | BRAUNIG_VHB6CT8 | 12/23/2022 13:15 | 12/24/2022 9:28 | Watch for extreme cold weather
12/23/2022 12:51 | BRAUNIG_VHB6CT6 | 12/23/2022 13:15 | 12/24/2022 9:28 | Watch for extreme cold weather
12/23/2022 18:16 | BRAUNIG_VHB6CT5 | 12/23/2022 18:17 | 12/24/2022 9:27 | Watch for extreme cold weather
12/23/2022 19:30 | STEAM_STEAM_2 | 12/24/2022 12:00 | 12/25/2022 12:00 | Watch for extreme cold weather
12/23/2022 19:32 | STEAM_STEAM_3 | 12/24/2022 12:00 | 12/25/2022 12:00 | Watch for extreme cold weather

## Slide 6: Real-Time Reserves and Pricing during the FFSS Deployment
The High Sustained Limit (HSL) of Resources deployed for FFSS is excluded from the on-line ORDC reserves
Chart: On-Line Operating Reserve Demand Curve (ORDC) Reserves during the FFSS Deployment

## Slide 7: Real-Time Reserves and Pricing during the FFSS Deployment
Chart: Real-Time On-Line ORDC Prices during the FFSS Deployment
Chart: Real-Time Off-Line ORDC Prices during the FFSS Deployment

## Slide 8: Restoring FFSS Reserves
Due to the timing of the FFSS deployment within the obligation period and the on-going potential for extreme cold weather and natural gas supply disruptions, QSEs for FFSSRs that were deployed were given instruction/approval to restock fuel reserves for FFSS.
A report will be provided on this topic after the end of the FFSS obligation period, as required by Protocol.

## Slide 9: Observed Issues and Lessons Learned
As noted in a Market Notice on December 30, ‘22, there was a failure to notify all Market Participants of the FFSS deployment, as required under Protocol.
  This error was solved with system changes implemented on January 12, ’23.
In preparing for the next FFSS obligation period in the latter part of ‘23, ERCOT staff has begun drafting Protocols to improve the existing language. Some of these items were lessons learned during the December deployment. Areas of improvement include:
  Process for approving/instructing the restocking of FFSS fuel;
  Process for QSEs performing FFSS testing;
  FFSS offer disclosure reporting;
  Incorporating the concept of an alternative Resource for FFSS throughout the language; and
  Various administrative clean-ups.