## Slide 1
PDCWG Report to ROS
Chair: Jimmy Jackson, CPS
Vice Chair: Vacant
ROS
Feb 2nd, 2023

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-2 FMEs and IMFR
    1 FME in the month of Dec
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 1/18/2023
  PDCWG Administrative Business
  IFRO OY2023 Change
  Updates to Business Practice Manual for QSEs Regarding ESRs
  ERCOT Reports
  TRE Report

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There was 1 FME in December
  12/7/2022 03:50:10
    Reduction of 1,400 MW of load
    Interconnection Frequency Response: 1,207 MW/0.1 Hz
    294 Resources were evaluated. These includes,
      262 Generation Resources
      0 Controllable Load Resources
      32 Energy Storage Resources
    114 of 294 Evaluated Resources had less than 75% of their expected Initial Primary Frequency Response.
    99 of 294 Evaluated Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 412 MW/0.1 Hz
IMFR Performance currently
1461.27 MW/0.1HZ

## Slide 7
Questions?

## Slide 8: Frequency Control Report
Dec 2022

## Slide 9: CPS1 Performance
Current 12-Month Rolling Average: 173.42%

## Slide 10: RMS1 Performance of ERCOT Frequency
Notes: 14.80Mhz on avg for Dec 2022

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections

## Slide 13: ERCOT Total Energy
Notes: 33,862,352 MWh

## Slide 14: ERCOT Total Energy from Wind Generation
Notes:   8,586,488 MWH

## Slide 15: ERCOT % Energy from Wind Generation
Notes: 25.36%

## Slide 16: ERCOT Total Energy from Solar Generation
Notes: 1,171,432 MWh

## Slide 17: ERCOT % Energy from Solar Generation
Notes: 3.46%

## Slide 18: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia =123,509 MW*s on 10/22/2022
Previous Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 209,794 MW*s
Max: 342,396 MW*s on Dec 23rd
Min: 144,718 MW*s on Dec 13th

## Slide 19: ERCOT Inertia Trend
Notes: For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.