## Slide 1
ROS | February 2nd, 2022
Alex Lee
ERCOT
Grid Analysis
Nov. Operations Report Follow-Up

## Slide 2: 1. Section 2.1: Frequency Events
Question: Why did the November 18 event frequency recovery take over 6 minutes and is it a concern?
  Almost 200 MW of run-back followed by the trip (329 MW).
  No RRS was deployed (did not hit the 59.91 Hz).
  Event occurred between the SCED runs.
  All 163 MW of Regulation Up was deployed.
  Wind Generation was ramping down ~125 MW.
  Frequency recovered to 59.965 Hz within 20 seconds.
  NERC frequency recovery obligation is 15 minutes, and the frequency recovery time was not a reliability concern.
Date and Time | Delta Frequency | Max/Min Frequency | Duration of Event | PMU Data |  | MW Loss | Load | IRR | Inertia
 | (Hz) | (Hz) |  | Oscillation Mode (Hz) | Damping Ratio |  | (MW) | % | (GW-s)
11/18/2022 1:02:16 | 0.077 | 59.936 | 00:06:20 | 0.67 | 9% | 329 | 40,427 | 42% | 220,447
Reporting Criteria: Delta Frequency is 60 mHz or greater; the MW loss is 350 MW or greater; or resource trip event triggered RRS deployment.

## Slide 3: 2. Section 5: Largest Net-Load Ramps
Question: Could ERCOT add Interval Ending (IE) to the Largest Net-Load Ramps.
  IEs are added to the report month and “All months in 2014-2022” (last two rows).
Month and Year | 5 min | 10 min | 15 min | 30 min | 60 min
December 2014 | 1,014 MW | 1,689 MW | 2,112 MW | 3,034 MW | 5,296 MW
December 2015 | 962 MW | 1,637 MW | 1,995 MW | 3,241 MW | 5,516 MW
December 2016 | 857 MW | 1,404 MW | 1,827 MW | 3,166 MW | 5,866 MW
December 2017 | 964 MW | 1,581 MW | 2,078 MW | 3,393 MW | 5,708 MW
December 2018 | 923 MW | 1,553 MW | 2,148 MW | 4,109 MW | 7,218 MW
December 2019 | 1,014 MW | 1,689 MW | 2,112 MW | 3,034 MW | 5,296 MW
December 2020 | 1,083 MW | 1,780 MW | 2,479 MW | 5,882 MW | 10,364 MW
December 2021 | 933 MW | 1,518 MW | 2,154 MW | 4,103 MW | 7,128 MW
December 2022 | 1,138 MW 12/31/22 (IE 16:51) | 1,981 MW 12/14/22 (IE 16:48) | 2,841 MW 12/14/22 (IE 16:48) | 5,459 MW 12/14/22 (IE 17:10) | 10,490 MW 12/14/22 (IE 17:24)
All Months in 2014-2022 | 1,647 MW 05/25/22 (IE 17:06) | 2,155 MW 03/24/22 (IE 19:05) | 3,015 MW 03/24/22 (IE 19:10) | 5,882 MW 03/24/22 (IE 19:10) | 10,750 MW 03/24/22 (IE 19:27)

## Slide 4: 3. Section 6: COP Error Analysis
Question: Why did the COP Error switch between over-scheduling and under-scheduling during the Operating Day? Is this accurate?
  Mean Absolute Error (MAE) is used for the magnitude of the Bar Chart.
  Average Error is used to determine over-scheduling vs. under-scheduling.
Example:
            MAE = (300+200+200+200+150) / 5 = 1050 / 5 = 210
            Average Error = (-300-200+200+200+150) / 5 = 50 / 5
            = 10 (over-scheduling error)
            If the Error for Hour 5 changes from to 150 to 50,
            MAE = (300+200+200+200+50) / 5 = 950 / 5 = 190
            Average Error = (-300-200+200+200+50) / 5 = -50 / 5
            = -10 (under-scheduling error)
Hour | Error
1 | -300
2 | -200
3 | 200
4 | 200
5 | 150

## Slide 5: 3. Section 6: COP Error Analysis (Continued)
Mean Absolute Error (MAE) vs Average Error.
Near real-time, COP Error is small in magnitude and may change between over-scheduling and under-scheduling based on COP submissions.
Chart: COP Error: MAE vs. Average Error (Dec. 2022)
| DA 0:00 | DA 1:00 | DA 2:00 | DA 3:00 | DA 4:00 | DA 5:00 | DA 6:00 | DA 7:00 | DA 8:00 | DA 9:00 | DA 10:00 | DA 11:00 | DA 12:00 | DA 13:00 | DA 14:00 | DA 15:00 | DA 16:00 | DA 17:00 | DA 18:00 | DA 19:00 | DA 20:00 | DA 21:00 | DA 22:00 | DA 23:00 | OD 0:00 | OD 1:00 | OD 2:00 | OD 3:00 | OD 4:00 | OD 5:00 | OD 6:00 | OD 7:00 | OD 8:00 | OD 9:00 | OD 10:00 | OD 11:00 | OD 12:00 | OD 13:00 | OD 14:00 | OD 15:00 | OD 16:00 | OD 17:00 | OD 18:00 | OD 19:00 | OD 20:00 | OD 21:00 | OD 22:00 | OD 23:00
Mean Absolute Error (MAE) | 11978.2981 | 11991.2668 | 11994.6862 | 11994.6862 | 11995.912 | 11983.7816 | 11919.112 | 12013.9069 | 11786.4129 | 10917.4505 | 10000.6298 | 9999.3886 | 9985.6897 | 6272.9023 | 2283.2829 | 1486.6429 | 1164.0749 | 1110.0056 | 1122.1539 | 1078.3766 | 1023.5022 | 1088.0309 | 1032.1813 | 989.743 | 975.2339 | 938.5488 | 940.4312 | 937.8484 | 934.2925 | 900.1935 | 890.0038 | 838.4546 | 830.2946 | 783.2038 | 730.5466 | 689.9702 | 665.8379 | 624.4001 | 615.4585 | 602.6719 | 586.668 | 581.7304 | 564.6405 | 554.3606 | 556.0745 | 556.9035 | 553.4989 | 553.4989
Average Error | -11808.9317 | -11821.9004 | -11825.3198 | -11825.3198 | -11826.5456 | -11814.4152 | -11738.3208 | -11835.1676 | -11626.4839 | -10799.4476 | -9934.7823 | -9933.5276 | -9919.8286 | -6005.0563 | -81.681 | 766.4026 | 596.3101 | 392.8632 | 435.2394 | 403.5427 | 298.0075 | 348.2481 | 309.0983 | 320.6358 | 314.057 | 243.5168 | 243.157 | 213.8169 | 207.257 | 203.3363 | 210.7659 | 163.4511 | 107.9255 | 59.2817 | 18.5265 | 29.1067 | 20.1081 | -10.33 | -6.2238 | -36.7173 | -74.1522 | -78.0556 | -64.9509 | -68.1238 | -67.4218 | -71.5315 | -74.5699 | -74.5699
Chart: COP Error: MAE vs. Average Error (Dec. 2022)
| DA 14:00 | DA 15:00 | DA 16:00 | DA 17:00 | DA 18:00 | DA 19:00 | DA 20:00 | DA 21:00 | DA 22:00 | DA 23:00 | OD 0:00 | OD 1:00 | OD 2:00 | OD 3:00 | OD 4:00 | OD 5:00 | OD 6:00 | OD 7:00 | OD 8:00 | OD 9:00 | OD 10:00 | OD 11:00 | OD 12:00 | OD 13:00 | OD 14:00 | OD 15:00 | OD 16:00 | OD 17:00 | OD 18:00 | OD 19:00 | OD 20:00 | OD 21:00 | OD 22:00 | OD 23:00
Mean Absolute Error (MAE) | 2283.2829 | 1486.6429 | 1164.0749 | 1110.0056 | 1122.1539 | 1078.3766 | 1023.5022 | 1088.0309 | 1032.1813 | 989.743 | 975.2339 | 938.5488 | 940.4312 | 937.8484 | 934.2925 | 900.1935 | 890.0038 | 838.4546 | 830.2946 | 783.2038 | 730.5466 | 689.9702 | 665.8379 | 624.4001 | 615.4585 | 602.6719 | 586.668 | 581.7304 | 564.6405 | 554.3606 | 556.0745 | 556.9035 | 553.4989 | 553.4989
Average Error | -81.681 | 766.4026 | 596.3101 | 392.8632 | 435.2394 | 403.5427 | 298.0075 | 348.2481 | 309.0983 | 320.6358 | 314.057 | 243.5168 | 243.157 | 213.8169 | 207.257 | 203.3363 | 210.7659 | 163.4511 | 107.9255 | 59.2817 | 18.5265 | 29.1067 | 20.1081 | -10.33 | -6.2238 | -36.7173 | -74.1522 | -78.0556 | -64.9509 | -68.1238 | -67.4218 | -71.5315 | -74.5699 | -74.5699