## Slide 1
LFL-47
Consider Voltage Control/Stability impacts

## Slide 2: LFL-47 Consider Voltage Control/Stability impacts
Consider the impacts of LFL’s interval behavior on voltage control and/or voltage stability.
  Do variances in LFL consumption cause transmission connected substation voltage to vary?
  Do variances in LFL consumption cause the need for additional reactive switching of existing reactive devices?

## Slide 3: LFL-47 Consider Voltage Control/Stability impacts
Variance in voltage relative to system conditions
  Evaluated 4 of the current LFLs
    Size
    Location - POI Strength
    On Peak
    Off Peak

## Slide 4: On Peak

## Slide 5: Real-Time Case – Summer Peak
Study Date/Time: 07/20/2022 at 16:52 CDT
System Load: 86,138 MW
Total Wind: 7,754 MW
Total Solar: 8,156 MW
LFL-A Bus Voltage (kV) Central Texas |  | Number of Capacitors in Service (6 at LFL_A) |  | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 3 | 6
LFL load amount as % of max consumption | 0% | 138.9 kV | 140.7 kV | 142.5 kV
70 | 10% | 138.8 kV | 140.6 kV | 142.4 kV
300 | 90% | 138.5 kV | 140.3 kV | 142.1 kV
370 | 100% | 138.4 kV | 140.1 kV | 141.9 kV

## Slide 6: Real-Time Case – Winter Peak
Study Date/Time: 12/23/2022 at 07:31 CDT
System Load: 79,272 MW
Total Wind: 12,339 MW
Total Solar: 64 MW
LFL-A Bus Voltage (kV) Central Texas |  | Number of Capacitors in Service (6 at LFL-A) |  | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 3 | 6
LFL load amount as % of max consumption | 0% | 139.9 kV | 141.6 kV | 143.5 kV
70 | 10% | 139.8 kV | 141.6 kV | 143.4 kV
300 | 90% | 138.6 kV | 140.4 kV | 142.2 kV
370 | 100% | 138.6 kV | 140.4 kV | 142.2 kV

## Slide 7: Real-Time Case – Summer Peak
Study Date/Time: 07/20/2022 at 16:52 CDT
System Load: 86,138 MW
Total Wind: 7,754 MW
Total Solar: 8,156 MW
LFL-B Bus Voltage (kV) Pan Handle |  | Number of Capacitors in Service (2 at Station-1) | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 2
LFL load amount as % of max consumption | 0% | 357.7 kV | 358.5 kV
70 | 50% | 357.6 kV | 358.4 kV
370 | 100% | 357.6 kV | 358.3 kV

## Slide 8: Real-Time Case – Winter Peak
Study Date/Time: 12/23/2022 at 07:31 CDT
System Load: 79,272 MW
Total Wind: 12,339 MW
Total Solar: 64 MW
LFL-B Bus Voltage (kV) Pan Handle |  | Number of Capacitors in Service (2 at Station-1) | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 2
LFL load amount as % of max consumption | 0% | 359.5 kV | 360.8 kV
70 | 50% | 359.4 kV | 360.8 kV
370 | 100% | 359.4 kV | 360.8 kV

## Slide 9: Real-Time Case – Summer Peak
Study Date/Time: 07/20/2022 at 16:52 CDT
System Load: 86,138 MW
Total Wind: 7,754 MW
Total Solar: 8,156 MW
LFL-C Bus Voltage (kV) West Texas |  | Number of Capacitors in Service (4 at LFL-C) |  |  |  | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 1 | 2 | 3 | 4
LFL load amount as % of max consumption | 0% | 141.6 kV | 143.3 kV | 146.3 kV | 149.5 kV | 152.9 kV
70 | 33% | 140.7 kV | 142.4 kV | 145.4 kV | 148.6 kV | 151.9 kV
370 | 66% | 139.6 kV | 141.2 kV | 144.3 kV | 147.4 kV | 150.8 kV
 | 100% | 136.9 kV | 139.8 kV | 142.9 kV | 146 kV | 149.3 kV

## Slide 10: Real-Time Case – Winter Peak
Study Date/Time: 12/23/2022 at 07:31 CDT
System Load: 79,272 MW
Total Wind: 12,339 MW
Total Solar: 64 MW
LFL-C Bus Voltage (kV) West Texas |  | Number of Capacitors in Service (4 at LFL-C) |  |  |  | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 1 | 2 | 3 | 4
LFL load amount as % of max consumption | 0% | 142.6 kV | 145 kV | 147.4 kV | 149.9 kV | 152.4 kV
70 | 33% | 142 kV | 144.3 kV | 146.7 kV | 149.2 kV | 151.8 kV
370 | 66% | 141.2 kV | 143.6 kV | 146 kV | 148.4 kV | 151 kV
 | 100% | 140.3 kV | 142.6 kV | 145 kV | 147.5 kV | 150 kV
Notes: EMS_RT_20221223_0731_HV_LILI

## Slide 11: Real-Time Case – Summer Peak
Study Date/Time: 07/20/2022 at 16:52 CDT
System Load: 86,138 MW
Total Wind: 7,754 MW
Total Solar: 8,156 MW
LFL-D Bus Voltage (kV) West Texas |  | Number of Capacitors in Service (3 at Station-2) |  |  | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 1 | 2 | 3
LFL load amount as % of max consumption | 0% | 142.5 kV | 143.2 kV | 144 kV | 144.8 kV
70 | 100% | 141.9 kV | 142.7 kV | 143.5 kV | 144.3 kV

## Slide 12: Real-Time Case – Winter Peak
Study Date/Time: 12/23/2022 at 07:31 CDT
System Load: 79,272 MW
Total Wind: 12,339 MW
Total Solar: 64 MW
LFL-D Bus Voltage (kV) West Texas |  | Number of Capacitors in Service (3 at Station-2) |  |  | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 1 | 2 | 3
LFL load amount as % of max consumption | 0% | 143 kV | 143.8 kV | 144.6 kV | 145.5 kV
70 | 100% | 142.3 kV | 143.2 kV | 144 kV | 144.8 kV
Notes: EMS_RT_20221223_0731_HV_LILI

## Slide 13: Off Peak

## Slide 14: Real-Time Case – Winter Off Peak
LFL-A Bus Voltage (kV) Central Texas |  | Number of Capacitors in Service (6 at LFL-A) |  | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 3 | 6
LFL load amount as % of max consumption | 0% | 142.1 kV | 142.3 kV | 145.6 kV
70 | 10% | 140.9 kV | 144.0 kV | 145.3 kV
300 | 90% | 138.1 kV | 141.3 kV | 142.5 kV
370 | 100% | 137.6 kV | 139.8 kV | 142.0 kV
Study Date/Time: 01/17/2023 at 11:42 CDT
System Load: 46,620 MW
Total Wind: 2,780 MW
Total Solar: 6,184 MW
Notes: SNDSW XFMR1 – 600 Max MW
SNDOW LD_ALCOA – 70 Max MW
Basecase violations are caused when scenario is in RED on table
1/17/2023 at 11:42 am:
Lowest WIND (2744.7 MW)
Solar (6,044 MW)
18266 and 18267 caps at SNDSW do not turn on when you want to turn on all the 6 caps at this station and the XFMR1 and LC_ALCOA loads are 0 or 0/70 MW scenarios. In total there are only 4 caps online. On the other hand, 5 capacitors are online for 300/0 and 370 MW scenarios.
Making 431 and 421 lines out with 370 MW load for XFMR1 and LD_ALCOA without caps voltage at SNDSW is 136 kV, after adding 6 caps was 140.7 KV

## Slide 15: Real-Time Case – Winter Off Peak
LFL-A Bus Voltage (kV) Central Texas |  | Number of Capacitors in Service (6 at LFL-A) |  | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 3 | 6
LFL load amount as % of max consumption | 0% | 141.3 kV | 142.5 kV | 145.8 kV
70 | 10% | 141.1 kV | 142.3 kV | 145.5 kV
300 | 90% | 138.3 kV | 140.5 kV | 142.7 kV
370 | 100% | 138.8 kV | 140.0 kV | 142.2 kV
Study Date/Time: 01/19/2023 at 0244 CDT
System Load: 39,656 MW
Total Wind: 19,622 MW
Total Solar: 16 MW
Notes: SNDSW XFMR1 – 600 Max MW
SNDOW LD_ALCOA – 70 Max MW
******Change to % of total site load
Basecase violations are caused when scenario is in RED on table
1/17/2023 at 11:41 am:
Lowest WIND (2744.7 MW)
Solar (6,044 MW)
18266 and 18267 caps at SNDSW do not turn on when you want to turn on all the 6 caps at this station and the XFMR1 and LC_ALCOA loads are 0 or 0/70 MW scenarios. In total there are only 4 caps online. On the other hand, 5 capacitors are online for 300/0 and 370 MW scenarios.
Making 431 and 421 lines out with 370 MW load for XFMR1 and LD_ALCOA without caps voltage at SNDSW is 136 kV, after adding 6 caps was 140.7 KV

## Slide 16: Real-Time Case – Winter Off Peak
Study Date/Time: 01/17/2023 at 11:42 CDT
System Load: 46,620 MW
Total Wind: 2,780 MW
Total Solar: 6,184 MW
LFL-B Bus Voltage (kV) Pan Handle |  | Number of Capacitors in Service (2 at Station-1) | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 2
LFL load amount as % of max consumption | 0% | 358.7 kV | 360.2 kV
70 | 50% | 358.6 kV | 360.1 kV
370 | 100% | 358.5 kV | 360.0 kV
Notes: 1/17/2023 at 11:42 am:
Lowest WIND (2744.7 MW)
Solar (6,044 MW)

## Slide 17: Real-Time Case – Winter Off Peak
Study Date/Time: 01/19/2023 at 0244 CDT
System Load: 39,656 MW
Total Wind: 19,622 MW
Total Solar: 16 MW
LFL-B Bus Voltage (kV) Pan Handle |  | Number of Capacitors in Service (2 at Station-1) | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 2
LFL load amount as % of max consumption | 0% | 358.2 kV | 359.3 kV
70 | 50% | 358.2 kV | 359.3 kV
370 | 100% | 358.2 kV | 359.4 kV
Notes: 1/19/2023 at 02:44 am:
Lowest WIND (19,393 MW)
Solar (0.1733 MW)

## Slide 18: Real-Time Case – Winter Off Peak
Study Date/Time: 01/17/2023 at 11:57 CDT
System Load: 43,121 MW
Total Wind: 3,014 MW
Total Solar: 6,339 MW
LFL-C Bus Voltage (kV) West Texas |  | Number of Capacitors in Service (4 at LFL-C) |  |  |  | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 1 | 2 | 3 | 4
LFL load amount as % of max consumption | 0% | 141.5 kV | 143.9 kV | 146.3 kV | 148.7 kV | 151.3 kV
70 | 33% | 140.9 kV | 143.2 kV | 145.6 kV | 148.1 kV | 150.6 kV
370 | 66% | 140.1 kV | 142.4 kV | 144.8 kV | 147.2 kV | 149.8 kV
 | 100% | 139.1 kV | 141.4 kV | 143.8 kV | 146.3 kV | 148.8 kV

## Slide 19: Real-Time Case – Winter Off Peak
Study Date/Time: 01/17/2023 at 11:57 CDT
System Load: 43,121 MW
Total Wind: 3,014 MW
Total Solar: 6,339 MW
LFL-D Bus Voltage (kV) West Texas |  | Number of Capacitors in Service (3 at Station-2) |  |  | 
Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | Total Load MW (SNDSW XFMR1 and SNDOW LD_ALCOA) | 0 | 1 | 2 | 3
LFL load amount as % of max consumption | 0% | 142.2 kV | 143.1 kV | 143.9 kV | 144.8 kV
70 | 100% | 141.6 kV | 142.4 kV | 143.2 kV | 144.1 kV
Notes: All Load at LONESTAR at 0 MW, ALL caps on at LONESTAR, All caps OFF at PCOVE, GEMCRY_1 at 0 MW = 143.4 kV NO voltage violation
All Load at LONESTAR Loads at 160 MW, ALL caps on at LONESTAR, BCGWRW_1 at 80 MW, All caps ON at PCOVE, GEMCRY_1 at 80 MW = 144.8 kV NO voltage violation
All Load at LONESTAR at 0 MW, ALL caps on at LONESTAR, All caps ON at PCOVE, GEMCRY_1 at 0 MW = 145.9 kV HIGH VOLTAGE VIOLATION
All Load at LONESTAR at 0 MW, ALL caps on at LONESTAR, All caps ON at PCOVE, GEMCRY_1 at 80 MW = 145.3 kV HIGH VOLTAGE VIOLATION

## Slide 20: Takeaway
At this time, current operational procedures appear to be sufficient to handle Large Load fluctuations.