## Slide 1: LFLTF Issues: Item 35 - Outage Coordination
Background – Prior Outage Coordination questions:
How is the LFL required to register?
Will the LFL provide Ancillary Services?
What is the interconnection topology (Non-breaker/Breaker Station/TIF)?
How will ERCOT handle Summer Outage Restriction exemptions?
Are changes to the Planning process needed to identify and mitigate potential congestion issues for maintenance outage conditions (N-1-1)?
What assumption(s) will ERCOT make for LFLs in the Outage Coordination study?
Operations | LFL-35 | Consider what changes to outage coordination processes are needed to incorporate LFL, including load assumptions for outage coordination studies.

## Slide 2: LFLTF Issue: Item 35 - Outage Coordination
Many of the Outage Coordination process concerns are address so long as the following items are satisfied:
The LFL is registered as an LFL or has made known is intention to act as a flexible load prior to the Interconnection study [Q1]
The LFL is represented by a QSE which will be responsible for the LFL’s activities related (but not limited) to Ancillary Services and Outage Request submittals to ERCOT [Q2]
The TSP requires a breakered facility, which would be owned by the interconnecting TSP. (no hard taps) [Q3]
In addition, these assume that the Planning process for LFL follows a similar process as GINR in which transmission security concerns are not relieved by proposing Transmission upgrades but rather the customer is assumed to reduce load consumption to mitigate the security concerns.
Lastly, while not directly related to LFL-35, the LFL should have the capability to perform under-frequency and manual load shed via non-transmission level breakers. This would also allow BES connectivity to remain.

## Slide 3: LFLTF Issues: Item 35 - Outage Coordination
Q4: Summer Outage restriction exemptions:
TSPs are limited to taking outages during non-Summer months (October – April)
Consider: In order to achieve the requested interconnection schedule, Summer Outage restriction exemptions will likely be needed – would interconnecting LFLs be granted Summer Outage restriction exemptions?
Notes: Technically Summer Restriction period is May 15 to September 15, but loads are too high May 1 through September 15th and probability of outage cancellation is very high.

## Slide 4: LFLTF Issues: Item 35 - Outage Coordination
Q5: Mitigating Congestion Issues via Planning Process:
The Planning process should follow the Generation interconnection process based on the Load’s flexibility as well as maintenance outage performance.
  Will the LFL be required to come offline completely to allow maintenance outage? If not, then LSL capacity should be planned for to be able to serve the minimum load remaining.
Consider: How do LFLs work with PGRR098, Consideration of Load Shed in Transmission Planning Criteria?

## Slide 5: LFLTF Issues: Item 35 - Outage Coordination
Q6: Considerations for Outage Coordination Studies
Increase transparency of the assumptions made for Outage Coordination Studies.
Build in flexibility to allow modifications to Dispatch, even after the Outage Coordination case is built.
  Nodal Protocol Section 3.1.5.11 Evaluation of Transmission Facilities Planned Outage or Maintenance Outage Requests outlines the different factors that are to be considered for the Outage Coordination case, but once the case is built there are little to no modifications that can be made to allow a Transmission Outage to move forward.
  Example: If a hot spell or something unusual happened during the proxy time window ERCOT uses in the study, the case may have an unusual dispatch in which a generator that doesn’t typically run off-peak, is running. Therefore, the outage is rejected and recommended to be rescheduled at a different time. Having the mechanisms available to mitigate dispatch issues in real-time should be included in the Outage Coordination Studies (RUC).
Will the Outage Scheduling process have a way to determine loads that are flexible within the case so they know to scale down? If so, then the Loads should be flexed as appropriate to help with Outage Coordination scheduling.

## Slide 6: Questions?