## Slide 1
Update on Operations-Related Items
Jeff Billo
Operations
ERCOT
Large Flexible Load Task Force
February 17, 2023
ERCOT Public

## Slide 2: Items under discussion internally at ERCOT
LFL-32: Identify technical requirements for ramp-rate limitations.
  Current thinking:
    CLRs will have a ramp-rate limitation of 20%/minute to align with SCED interval.
    Everything else will need a significantly slower limitation to mitigate reliability impact. Could have different limitations for ramping down (less risk) and ramping up (more risk).
      See October LFLTF presentation: https://www.ercot.com/files/docs/2022/10/21/LFLTF_Operations_Requirements_Oct2022.pptx
LFL-45: Identify impacts to load forecasting and consider what process changes are necessary to incorporate LFL.
  Current thinking: develop hourly LFL forecast model based on predicted prices and incorporate results into operational load forecast models.
Price Forecast
LFL Forecast
MTLF

## Slide 3: Items under discussion internally at ERCOT
LFL-46: Consider impact of large flexible loads tripping in light-load conditions.
  Main impact may be to frequency stability due to simultaneous tripping for a ride-through event.
Recent Ride-Through Events (1/2):
  October 12, 2022, 05:56 – Load Loss
    Event initiated by multiple faults at a 345-kV substation in West Texas
    ~415 MW of load reduction in West Texas due to low voltage
    Frequency spiked to 60.086 Hz
  October 31, 2022, 12:12 - Load Loss
    Event initiated by multiple faults at a 345/138-kV substation in the DFW area
    ~500 MW of load reduction throughout the system due to low voltage
    Frequency spiked to 60.132 Hz
    ~869 MW of thermal generation loss at two plants

## Slide 4: Items under discussion internally at ERCOT
Recent Ride-Through Events (2/2):
  December 7, 2022, 03:50 – Load Loss
    Event initiated by multiple faults at a 138-kV substation in West Texas
    ~1,560 MW of load reduction in West Texas
    Frequency spiked to 60.235 Hz
    ~112 MW of thermal generation loss at two plants
  January 23, 2023, 12:19 – IBR and Load Loss
    Event initiated by a normally-cleared fault on a 138-kV line in West Texas
    ~298 MW of solar generation loss at 8 plants
    ~208 MW of load reduction at four Large Flexible Load (LFL) sites
    Event is still under investigation
Voltage ride-through reductions at large loads is an emerging issue.

## Slide 5: Other items
LFL-36: Determine if and how LFL should be taken into account in the AS methodology, including any site-specific maximum limit.
  Protocol 3.16(2): “ERCOT shall, at least annually, determine with supporting data, the methodology for determining the quantity requirements for each Ancillary Service needed for reliability…”
  ERCOT will bring any potential methodology changes necessary to account for LFLs to stakeholders as part of the normal AS methodology review process.
    Recommend marking this item as closed.
LFL-47: Consider voltage control / voltage stability impacts of LFL interval behavior.
  Separate presentation at this meeting.